## Sheet 1
Date & Time | Iteration | Sample Location | pH (SCADA) | pH (benchtop) | Turbidity (sc100) | Turbidity (benchtop) | UVT (benchtop) | Colour (benchtop) | Mn (HW Lab) | Fe (benchtop) | Al (benchtop) | Alkalinity (HW Lab) | Filter Run Times (hrs) | Filter Head Loss (ft) | Alum Dose (mg/L) | Floc Time | Coagulant Type | KMnO4 Dose | Oxidation Time (KMnO4 dosing configuration) | Filter Feed (gpm) | Filter 1 Media | Filter 2 Media | TOC @ CWRS | DOC @ CWRS | Notes
2022-04-29 08:51:00 AM | 1 | Raw | - | 5.09 | 0.39400000000000002 | 1.25 | 73.599999999999994 | 33 | - | 0.1 | 6.0999999999999999E-2 | - | - | - | 40 | 23 min | Alum | 0 | 0.5 | 5 | GAC | Anthracite
2022-04-29 08:52:00 AM | 1 | Rapid Mix | - | 5.92 | - | 1.73 | - | - | - | - | - | - | - | - | 40 | 23 min | Alum | 0 | 0.5 | 5 | GAC | Anthracite
2022-04-29 08:56:00 AM | 1 | DAF | 5.68 | 5.9 | 0.371 | 0.439 | 92.1 | 12 | - | 0.04 | 0.23799999999999999 | - | - | - | 40 | 23 min | Alum | 0 | 0.5 | 5 | GAC | Anthracite
2022-05-02 09:15:00 AM | 2 | Raw | - | 5.27 | 0.38 | 0.48599999999999999 | 73.7 | 30 | - | 0.09 | 0.05 | - | - | - | 40 | 23 min | Alum | 0 | 0.5 | 5 | GAC | Anthracite
2022-05-02 09:18:00 AM | 2 | Rapid Mix | - | 6.1 | - | 1.62 | - | - | - | - | - | - | - | - | 40 | 23 min | Alum | 0 | 0.5 | 5 | GAC | Anthracite
2022-05-02 09:21:00 AM | 2 | DAF | 6.18 | 6.14 | 0.312 | 0.50700000000000001 | 90.7 | 12 | - | 0.03 | 0.27700000000000002 | - | - | - | 40 | 23 min | Alum | 0 | 0.5 | 5 | GAC | Anthracite
2022-05-03 08:57:00 AM | 3 | Raw | - | 5.22 | 0.52 | 0.52800000000000002 | 74.3 | 33 | - | 0.09 | 4.5999999999999999E-2 | - | - | - | 40 | 23 min | Alum | 0 | 0.5 | 5 | GAC | Anthracite
2022-05-03 08:59:59 AM | 3 | Rapid Mix | - | 5.83 | - | 1.61 | - | - | - | - | - | - | - | - | 40 | 23 min | Alum | 0 | 0.5 | 5 | GAC | Anthracite
2022-05-03 09:01:00 AM | 3 | DAF | 5.41 | 5.81 | 0.24199999999999999 | 0.39800000000000002 | 93.5 | 11 | - | 0.02 | 0.248 | - | - | - | 40 | 23 min | Alum | 0 | 0.5 | 5 | GAC | Anthracite
2022-05-09 06:59:00 AM | 4 | Raw | - | 5.0599999999999996 | 0.49 | 0.50600000000000001 | 74.7 | 30 | - | 0.08 | 4.1000000000000002E-2 | - | - | - | 40 | 23 min | Alum | 0 | 0.5 | 5 | GAC | Anthracite
2022-05-09 06:59:59 AM | 4 | Rapid Mix | - | 5.44 | - | 1.65 | - | - | - | - | - | - | - | - | 40 | 23 min | Alum | 0 | 0.5 | 5 | GAC | Anthracite
2022-05-09 07:01:00 AM | 4 | DAF | 5.55 | 5.42 | 0.309 | 0.45200000000000001 | 92.9 | 9 | - | 7.0000000000000007E-2 | 0.254 | - | - | - | 40 | 23 min | Alum | 0 | 0.5 | 5 | GAC | Anthracite
2022-05-10 07:20:00 AM | 5 | Raw | - | 5.51 | 0.49 | 0.52700000000000002 | 74.400000000000006 | 31 | - | 0.06 | 4.1000000000000002E-2 | - | - | - | 40 | 23 min | Alum | 0 | 0.5 | 5 | GAC | Anthracite
2022-05-10 07:21:00 AM | 5 | Rapid Mix | - | 5.79 | - | 1.55 | - | - | - | - | - | - | - | - | 40 | 23 min | Alum | 0 | 0.5 | 5 | GAC | Anthracite
2022-05-10 07:22:00 AM | 5 | DAF | 5.61 | 5.72 | 0.22500000000000001 | 0.33500000000000002 | 94.9 | 6 | - | 0.01 | 0.23200000000000001 | - | - | - | 40 | 23 min | Alum | 0 | 0.5 | 5 | GAC | Anthracite
2022-05-10 11:05:00 AM | 6 | Raw | - | 5.56 | 0.49 | 0.50600000000000001 | 75.400000000000006 | 29 | - | 0.08 | 6.9000000000000006E-2 | - | - | - | 40 | 23 min | Alum | 0 | 0.5 | 5 | GAC | Anthracite
2022-05-10 11:04:00 AM | 6 | Rapid Mix | - | 5.81 | - | 1.45 | - | - | - | - | - | - | - | - | 40 | 23 min | Alum | 0 | 0.5 | 5 | GAC | Anthracite
2022-05-10 11:05:00 AM | 6 | DAF | 5.51 | 5.87 | 0.30599999999999999 | 0.504 | 89 | 12 | - | 0.02 | 0.31900000000000001 | - | - | - | 40 | 23 min | Alum | 0 | 0.5 | 5 | GAC | Anthracite
2022-05-10 11:06:00 AM | 6 | F1 | - | 5.96 | 0.109 | 0.112 | 99.1 | 0 | - | 0.01 | 6.9000000000000006E-2 | - | 0.2 | 0 | 40 | 23 min | Alum | 0 | 0.5 | 5 | GAC | Anthracite
2022-05-10 11:08:00 AM | 6 | F2 | - | 5.94 | 0.156 | 0.13 | 96.9 | 0 | - | 0 | 3.7999999999999999E-2 | - | 0.2 | 0 | 40 | 23 min | Alum | 0 | 0.5 | 5 | GAC | Anthracite
2022-05-12 10:55:00 AM | 7 | Raw | - | 5.23 | 0.47 | 0.47399999999999998 | 76.400000000000006 | 29 | - | 0.09 | 5.1999999999999998E-2 | - | - | - | 47.5 | 23 min | Alum | 0 | 0.5 | 5 | GAC | Anthracite
2022-05-12 10:56:00 AM | 7 | Rapid Mix | - | 5.82 | - | 1.75 | - | - | - | - | - | - | - | - | 47.5 | 23 min | Alum | 0 | 0.5 | 5 | GAC | Anthracite
2022-05-12 11:05:00 AM | 7 | DAF | 5.37 | 5.89 | 0.252 | 0.41799999999999998 | 90.9 | 9 | - | 0.03 | 0.29699999999999999 | - | - | - | 47.5 | 23 min | Alum | 0 | 0.5 | 5 | GAC | Anthracite
2022-05-13 07:18:00 AM | 8 | Raw | - | 5.43 | 0.47 | 0.48499999999999999 | 74.7 | 31 | - | 7.0000000000000007E-2 | 5.0999999999999997E-2 | - | - | - | 50 | 23 min | Alum | 0 | 0.5 | 5 | GAC | Anthracite
2022-05-13 07:18:00 AM | 8 | Rapid Mix | - | 5.65 | - | 1.65 | - | - | - | - | - | - | - | - | 50 | 23 min | Alum | 0 | 0.5 | 5 | GAC | Anthracite
2022-05-13 07:19:00 AM | 8 | DAF | 5.68 | 5.63 | 0.17399999999999999 | 0.252 | 94.8 | 7 | - | 0.02 | 0.19600000000000001 | - | - | - | 50 | 23 min | Alum | 0 | 0.5 | 5 | GAC | Anthracite
2022-05-13 07:21:00 AM | 8 | F1 | - | 5.25 | 6.7000000000000004E-2 | 0.21299999999999999 | 99 | 1 | - | 0.01 | 0.16300000000000001 | - | 0.2 |  | 50 | 23 min | Alum | 0 | 0.5 | 5 | GAC | Anthracite
2022-05-13 07:22:00 AM | 8 | F2 | - | 5.82 | 7.1999999999999995E-2 | 7.2999999999999995E-2 | 98.5 | 1 | - | 0 | 0.01 | - | 0.5 |  | 50 | 23 min | Alum | 0 | 0.5 | 5 | GAC | Anthracite
2022-05-13 11:03:00 AM | 9 | Raw | - | 5.47 | 0.47 | 0.48199999999999998 | 75.2 | 30 | - | 7.0000000000000007E-2 | 4.9000000000000002E-2 | - | - | - | 50 | 23 min | Alum | 0 | 0.5 | 5 | GAC | Anthracite
2022-05-13 11:04:00 AM | 9 | Rapid Mix | - | 5.89 | - | 1.45 | - | - | - | - | - | - | - | - | 50 | 23 min | Alum | 0 | 0.5 | 5 | GAC | Anthracite
2022-05-13 11:04:00 AM | 9 | DAF | 5.49 | 5.95 | 0.20399999999999999 | 0.35299999999999998 | 93.9 | 10 | - | 0.03 | 0.27800000000000002 | - | - | - | 50 | 23 min | Alum | 0 | 0.5 | 5 | GAC | Anthracite
2022-05-13 11:06:00 AM | 9 | F1 | - | 5.96 | 6.7000000000000004E-2 | 0.10299999999999999 | 99.8 | 0 | - | 0.01 | 2.3E-2 | - | 2.7 |  | 50 | 23 min | Alum | 0 | 0.5 | 5 | GAC | Anthracite
2022-05-13 11:08:00 AM | 9 | F2 | - | 5.91 | 5.6000000000000001E-2 | 8.5999999999999993E-2 | 98.6 | 2 | - | 0.01 | 2E-3 | - | 3 |  | 50 | 23 min | Alum | 0 | 0.5 | 5 | GAC | Anthracite
2022-05-16 07:21:00 AM | 10 | Raw | - | 5.38 | 0.45 | 0.45700000000000002 | 78.5 | 28 | - | 0.09 | 3.6999999999999998E-2 | - | - | - | 50 | 23 min | Alum | 0 | 0.5 | 5 | GAC | Anthracite
2022-05-16 07:21:00 AM | 10 | Rapid Mix | - | 5.71 | - | 1.52 | - | - | - | - | - | - | - | - | 50 | 23 min | Alum | 0 | 0.5 | 5 | GAC | Anthracite
2022-05-16 07:22:00 AM | 10 | DAF | 5.61 | 5.61 | 0.16200000000000001 | 0.26500000000000001 | 97.6 | 4 | - | 0.04 | 0.16900000000000001 | - | - | - | 50 | 23 min | Alum | 0 | 0.5 | 5 | GAC | Anthracite
2022-05-16 07:23:00 AM | 10 | F1 | - | 5.63 | 0.214 | 8.6999999999999994E-2 | 100 | 0 | - | 0.02 | 8.9999999999999993E-3 | - | 3.7 | 14.51 | 50 | 23 min | Alum | 0 | 0.5 | 5 | GAC | Anthracite
2022-05-16 07:24:00 AM | 10 | F2 | - | 5.68 | 3.9E-2 | 7.9000000000000001E-2 | 100 | 0 | - | 0 | 3.0000000000000001E-3 | - | 4 | 3.55 | 50 | 23 min | Alum | 0 | 0.5 | 5 | GAC | Anthracite
2022-05-16 10:48:00 AM | 11 | Raw | - | 5.45 | 0.46 | 0.47799999999999998 | 76.599999999999994 | 29 | - | 0.1 | 7.6999999999999999E-2 | - | - | - | 50 | 23 min | Alum | 0.15 | 0.5 | 5 | GAC | Anthracite
2022-05-16 10:49:00 AM | 11 | Rapid Mix | - | 6.05 | - | 1.61 | - | - | - | - | - | - | - | - | 50 | 23 min | Alum | 0.15 | 0.5 | 5 | GAC | Anthracite
2022-05-16 10:50:00 AM | 11 | DAF | 5.51 | 5.99 | 0.19500000000000001 | 0.308 | 97.1 | 5 | - | 0.04 | 0.23100000000000001 | - | - | - | 50 | 23 min | Alum | 0.15 | 0.5 | 5 | GAC | Anthracite
2022-05-16 10:51:00 AM | 11 | F1 | - | 5.98 | 4.2000000000000003E-2 | 8.4000000000000005E-2 | 100 | 0 | - | 0.02 | 1.0999999999999999E-2 | - | 6.4 | 14.62 | 50 | 23 min | Alum | 0.15 | 0.5 | 5 | GAC | Anthracite
2022-05-16 10:53:00 AM | 11 | F2 | - | 6.01 | 4.1000000000000002E-2 | 9.5000000000000001E-2 | 100 | 0 | - | 0.03 | 1.0999999999999999E-2 | - | 7.7 | 3.58 | 50 | 23 min | Alum | 0.15 | 0.5 | 5 | GAC | Anthracite
2022-05-17 07:17:00 AM | 12 | Raw | - | 5.45 | 4.4800000000000004 | 0.47699999999999998 | 77.2 | 28 | 3.3000000000000002E-2 | 0.11 | 4.7E-2 | - | - | - | 50 | 23 min | Alum | 0.15 | 0.5 | 5 | GAC | Anthracite
2022-05-17 07:17:00 AM | 12 | Rapid Mix | - | 5.83 | - | 1.61 | - | - | - | - | - | - | - | - | 50 | 23 min | Alum | 0.15 | 0.5 | 5 | GAC | Anthracite
2022-05-17 07:18:00 AM | 12 | DAF | 5.68 | 5.82 | 0.17599999999999999 | 0.28299999999999997 | 98.6 | 4 | 2.3E-2 | 0.03 | 0.191 | - | - | - | 50 | 23 min | Alum | 0.15 | 0.5 | 5 | GAC | Anthracite
2022-05-17 07:19:00 AM | 12 | F1 | - | 5.84 | 6.0999999999999999E-2 | 8.7999999999999995E-2 | 100 | 0 | 2.5000000000000001E-2 | 0.03 | 6.0000000000000001E-3 | - | 9.2 hours | 14.72 | 50 | 23 min | Alum | 0.15 | 0.5 | 5 | GAC | Anthracite
2022-05-17 07:21:00 AM | 12 | F2 | - | 5.87 | 4.4999999999999998E-2 | 8.3000000000000004E-2 | 100 | 0 | - | 0.03 | 6.0000000000000001E-3 | - | 9.5 hours | 3.83 | 50 | 23 min | Alum | 0.15 | 0.5 | 5 | GAC | Anthracite
2022-05-17 09:56:00 AM | 13 | Raw | - | 5.36 | 0.45500000000000002 | 0.496 | 77.099999999999994 | 28 | - | 0.1 | 3.9E-2 | - | - | - | 50 | 23 min | Alum | 0.15 | 0.5 | 5 | GAC | Anthracite | 3.5870000000000002
2022-05-17 09:56:00 AM | 13 | Rapid Mix | - | 5.97 | - | 1.7 | - | - | - | - | - | - | - | - | 50 | 23 min | Alum | 0.15 | 0.5 | 5 | GAC | Anthracite
2022-05-17 09:56:59 AM | 13 | DAF | 5.39 | 5.87 | 0.17100000000000001 | 0.26900000000000002 | 98.3 | 6 | - | 0.03 | 0.13300000000000001 | - | - | - | 50 | 23 min | Alum | 0.15 | 0.5 | 5 | GAC | Anthracite | 2.1070000000000002
2022-05-17 09:58:00 AM | 13 | F1 | - | 5.94 | 5.2999999999999999E-2 | 9.8000000000000004E-2 | 100 | 0 | - | 0.02 | 4.0000000000000001E-3 | - | 11.7 | 14.82 | 50 | 23 min | Alum | 0.15 | 0.5 | 5 | GAC | Anthracite | 1.756
2022-05-17 09:58:59 AM | 13 | F2 | - | 5.95 | 4.2000000000000003E-2 | 7.9000000000000001E-2 | 100 | 0 | - | 0.03 | 1E-3 | - | 12 | 3.89 | 50 | 23 min | Alum | 0.15 | 0.5 | 5 | GAC | Anthracite | 1.8
2022-05-27 05:54:00 AM | 14 | Raw | - | 5.37 | 0.47499999999999998 | 0.46500000000000002 | 70.099999999999994 | 29 | - | 0.09 | 3.3000000000000002E-2 | - | - | - | 50 | 23 min | Alum | 0 | 0.5 | 5 | GAC | Anthracite
2022-05-27 05:54:00 AM | 14 | Rapid Mix | - | 6.05 | - | 1.93 | - | - | - | - | - | - | - | - | 50 | 23 min | Alum | 0 | 0.5 | 5 | GAC | Anthracite
2022-05-27 05:55:00 AM | 14 | DAF | 5.81 | 5.98 | 0.19900000000000001 | 0.40600000000000003 | 87.6 | 7 | 1.7000000000000001E-2 | 0.04 | 0.216 | - | - | - | 50 | 23 min | Alum | 0 | 0.5 | 5 | GAC | Anthracite
2022-05-27 05:56:00 AM | 14 | F1 | - | 5.95 | 7.5999999999999998E-2 | 0.106 | 93.4 | 1 | 1.7999999999999999E-2 | 0.03 | 0.01 | - | 14.1 | 14.55 | 50 | 23 min | Alum | 0 | 0.5 | 5 | GAC | Anthracite
2022-05-27 05:58:00 AM | 14 | F2 | - | 5.94 | 6.4000000000000001E-2 | 9.7000000000000003E-2 | 91.8 | 1 | 1.4E-2 | 0.03 | 2E-3 | - | 14.5 | 4.12 | 50 | 23 min | Alum | 0 | 0.5 | 5 | GAC | Anthracite
2022-05-27 09:29:00 AM | 15 | Raw | - | 5.38 | 0.46899999999999997 | 0.46800000000000003 | 70.2 | 30 | - | 0.09 | 3.9E-2 | - | - | - | 50 | 23 min | Alum | 0.05 | 0.5 | 5 | GAC | Anthracite
2022-05-27 09:29:00 AM | 15 | Rapid Mix | - | 6.24 | - |  | - | - | - | - | - | - | - | - | 50 | 23 min | Alum | 0.05 | 0.5 | 5 | GAC | Anthracite
2022-05-27 09:30:00 AM | 15 | DAF | 5.58 | 6.28 | 0.25800000000000001 | 0.68300000000000005 | 81.5 | 9 | - | 0.04 | 0.29899999999999999 | - | - | - | 50 | 23 min | Alum | 0.05 | 0.5 | 5 | GAC | Anthracite
2022-05-27 09:31:00 AM | 15 | F1 | - | 6.23 | 5.2999999999999999E-2 | 9.6000000000000002E-2 | 91.7 | 1 | - | 0.03 | 2.3E-2 | - | 17.7 | 14.87 | 50 | 23 min | Alum | 0.05 | 0.5 | 5 | GAC | Anthracite
2022-05-27 09:32:00 AM | 15 | F2 | - | 6.16 | 4.8000000000000001E-2 | 8.8999999999999996E-2 | 91.3 | 1 | 1.4999999999999999E-2 | 0.02 | 6.0000000000000001E-3 | - | 18.100000000000001 | 4.82 | 50 | 23 min | Alum | 0.05 | 0.5 | 5 | GAC | Anthracite
2022-05-30 07:30:00 AM | 16 | Raw | - | 5.4 | 0.45600000000000002 | 0.53900000000000003 | 70.900000000000006 | 28 | 2.4E-2 | 0.09 | 5.2999999999999999E-2 | - | - | - | 50 | 23 min | Alum | 0.05 | 0.5 | 5 | GAC | Anthracite
2022-05-30 07:30:00 AM | 16 | Rapid Mix | - | 5.87 | - | 1.63 | - | - | - | - | - | - | - | - | 50 | 23 min | Alum | 0.05 | 0.5 | 5 | GAC | Anthracite
2022-05-30 07:30:00 AM | 16 | DAF | 5.33 | 5.79 | 0.156 | 0.27100000000000002 | 88.8 | 6 | 1.7999999999999999E-2 | 0.03 | 0.14299999999999999 | - | - | - | 50 | 23 min | Alum | 0.05 | 0.5 | 5 | GAC | Anthracite
2022-05-30 07:31:00 AM | 16 | F1 | - | 5.81 | 4.5999999999999999E-2 | 9.6000000000000002E-2 | 93.8 | 1 | 0.02 | 0.02 | 1E-3 | - | 20 | 14.41 | 50 | 23 min | Alum | 0.05 | 0.5 | 5 | GAC | Anthracite
2022-05-30 07:32:00 AM | 16 | F2 | - | 5.88 | 4.2999999999999997E-2 | 0.10199999999999999 | 92.2 | 1 | 1.7999999999999999E-2 | 0.02 | 1E-3 | - | 20.5 | 4.57 | 50 | 23 min | Alum | 0.05 | 0.5 | 5 | GAC | Anthracite
2022-05-30 10:29:00 AM | 17 | Raw | - | 5.42 | 0.46400000000000002 | 0.51 | 70.900000000000006 | 29 | - | 0.09 | 5.5E-2 | - | - | - | 60 | 23 min | Alum | 0.05 | 0.5 | 5 | GAC | Anthracite | 3.794
2022-05-30 10:29:00 AM | 17 | Rapid Mix | - | 6.16 | - | 1.69 | - | - | - | - | - | - | - | - | 60 | 23 min | Alum | 0.05 | 0.5 | 5 | GAC | Anthracite
2022-05-30 10:29:59 AM | 17 | DAF | 4.83 | 6.24 | 0.122 | 0.20899999999999999 | 88.8 | 5 | - | 0.02 | 0.216 | - | - | - | 60 | 23 min | Alum | 0.05 | 0.5 | 5 | GAC | Anthracite | 2.3519999999999999
2022-05-30 10:31:00 AM | 17 | F1 | - | 6.07 | 3.3000000000000002E-2 | 7.0999999999999994E-2 | 93.3 | 0 | - | 0.01 | 3.0000000000000001E-3 | - | 22.9 | 14.63 | 60 | 23 min | Alum | 0.05 | 0.5 | 5 | GAC | Anthracite | 1.798
2022-05-30 10:32:00 AM | 17 | F2 | - | 6.05 | 4.5999999999999999E-2 | 7.0000000000000007E-2 | 92.7 | 1 | - | 0.01 | 0 | - | 23.4 | 4.66 | 60 | 23 min | Alum | 0.05 | 0.5 | 5 | GAC | Anthracite | 1.911
2022-05-31 05:47:00 AM | 18 | Raw | - | 5.47 | 0.48599999999999999 | 0.47499999999999998 | 71.2 | 27 | - | 0.08 | 1.9E-2 | - | - | - | 60 | 23 min | Alum | 0.05 | 0.5 | 5 | GAC | Anthracite
2022-05-31 05:47:00 AM | 18 | Rapid Mix | - | 5.95 | - | 1.65 | - | - | - | - | - | - | - | - | 60 | 23 min | Alum | 0.05 | 0.5 | 5 | GAC | Anthracite
2022-05-31 05:48:00 AM | 18 | DAF | 5.72 | 5.94 | 0.13500000000000001 | 0.20100000000000001 | 89.8 | 3 | - | 0.03 | 0.14799999999999999 | - | - | - | 60 | 23 min | Alum | 0.05 | 0.5 | 5 | GAC | Anthracite
2022-05-31 05:49:00 AM | 18 | F1 | - | 5.89 | 8.5999999999999993E-2 | 7.0000000000000007E-2 | 93.3 | 1 | - | 0.03 | 7.0000000000000001E-3 | - | 25.6 | 15 | 60 | 23 min | Alum | 0.05 | 0.5 | 5 | GAC | Anthracite
2022-05-31 05:51:00 AM | 18 | F2 | - | 5.94 | 4.8000000000000001E-2 | 0.08 | 90.4 | 0 | - | 0.02 | 4.0000000000000001E-3 | - | 26 | 5.52 | 60 | 23 min | Alum | 0.05 | 0.5 | 5 | GAC | Anthracite
2022-05-31 09:56:00 AM | 19 | Raw | - | 5.61 | 0.51 | 0.50600000000000001 | 71.5 | 28 | - | 0.08 | 3.9E-2 | - | - | - | 60 | 23 min | Alum | 0.05 | 0.5 | 5 | GAC | Anthracite
2022-05-31 09:56:00 AM | 19 | Rapid Mix | - | 6.24 | - | 1.61 | - | - | - | - | - | - | - | - | 60 | 23 min | Alum | 0.05 | 0.5 | 5 | GAC | Anthracite
2022-05-31 09:56:59 AM | 19 | DAF | 5.57 | 6.18 | 0.16200000000000001 | 0.23200000000000001 | 88.6 | 6 | - | 0.03 | 0.248 | - | - | - | 60 | 23 min | Alum | 0.05 | 0.5 | 5 | GAC | Anthracite
2022-05-31 09:58:00 AM | 19 | F1 | - | 6.1 | 9.1999999999999998E-2 | 0.11799999999999999 | 91.9 | 2 | - | 0.03 | 3.2000000000000001E-2 | - | 29.6 | 15 | 60 | 23 min | Alum | 0.05 | 0.5 | 5 | GAC | Anthracite
2022-05-31 09:58:59 AM | 19 | F2 | - | 6.13 | 8.2000000000000003E-2 | 0.11899999999999999 | 90.8 | 3 | - | 0.03 | 5.3999999999999999E-2 | - | 30 | 5.92 | 60 | 23 min | Alum | 0.05 | 0.5 | 5 | GAC | Anthracite
2022-06-01 06:18:00 AM | 20 | Raw | - | 5.48 | 0.50900000000000001 | 0.47 | 71.5 | 27 | - | 0.08 | 4.2999999999999997E-2 | - | - | - | 60 | 23 min | Alum | 0 | 0.5 | 5 | GAC | Anthracite
2022-06-01 06:18:00 AM | 20 | Rapid Mix | - | 6.08 | - | 1.56 | - | - | - | - | - | - | - | - | 60 | 23 min | Alum | 0 | 0.5 | 5 | GAC | Anthracite
2022-06-01 06:19:00 AM | 20 | DAF | 5.71 | 5.97 | 0.13100000000000001 | 0.20499999999999999 | 89.6 | 5 | - | 0.03 | 0.16400000000000001 | - | - | - | 60 | 23 min | Alum | 0 | 0.5 | 5 | GAC | Anthracite
2022-06-01 06:20:00 AM | 20 | F1 | - | 5.98 | 4.9000000000000002E-2 | 9.1999999999999998E-2 | 92.7 | 1 | - | 0.03 | 8.9999999999999993E-3 | - | 31.9 | 15 | 60 | 23 min | Alum | 0 | 0.5 | 5 | GAC | Anthracite
2022-06-01 06:21:00 AM | 20 | F2 | - | 6.01 | 5.8000000000000003E-2 | 8.5000000000000006E-2 | 90.8 | 1 | - | 0.03 | 6.0000000000000001E-3 | - | 32.4 | 5.92 | 60 | 23 min | Alum | 0 | 0.5 | 5 | GAC | Anthracite
2022-06-02 08:08:00 AM | 21 | Raw | - | 5.47 | 0.49299999999999999 | 0.48599999999999999 | 71.3 | 29 | - | 0.08 | 3.5000000000000003E-2 | - | - | - | 60 | 7 min | Alum | 0 | 0.5 | 5 | GAC | Anthracite
2022-06-02 08:08:00 AM | 21 | Rapid Mix | - | 6.21 | - | 1.38 | - | - | - | - | - | - | - | - | 60 | 7 min | Alum | 0 | 0.5 | 5 | GAC | Anthracite
2022-06-02 08:09:00 AM | 21 | DAF | 5.51 | 6.18 | 0.375 | 0.41199999999999998 | 87.8 | 11 | - | 0.04 | 0.33700000000000002 | - | - | - | 60 | 7 min | Alum | 0 | 0.5 | 5 | GAC | Anthracite
2022-06-02 08:10:00 AM | 21 | F1 | - | 6.09 | - | 7.9000000000000001E-2 | 95.9 | 0 | - | 0.01 | 7.0000000000000001E-3 | - | 2 | 12.66 | 60 | 7 min | Alum | 0 | 0.5 | 5 | GAC | Anthracite
2022-06-02 08:11:00 AM | 21 | F2 | - | 6.13 | 4.5999999999999999E-2 | 6.6000000000000003E-2 | 94.7 | 0 | - | 0.01 | 6.0000000000000001E-3 | - | 2.4 | 0.85 | 60 | 7 min | Alum | 0 | 0.5 | 5 | GAC | Anthracite
2022-06-03 06:44:00 AM | 22 | Raw | - | 5.48 | 0.48599999999999999 | 0.47099999999999997 | 72.2 | 28 | 3.1E-2 | 0.09 | - | - | - | - | 60 | 7 min | Alum | 0.05 | 0.5 | 5 | GAC | Anthracite
2022-06-03 06:44:00 AM | 22 | Rapid Mix | - | 6.15 | - | 1.49 | - | - | - | - | - | - | - | - | 60 | 7 min | Alum | 0.05 | 0.5 | 5 | GAC | Anthracite
2022-06-02 06:45:00 AM | 22 | DAF | 5.64 | 6.14 | 0.38500000000000001 | 0.41899999999999998 | 85.8 | 12 | 2.3E-2 | 0.04 | - | - | - | - | 60 | 7 min | Alum | 0.05 | 0.5 | 5 | GAC | Anthracite
2022-06-03 06:46:00 AM | 22 | F1 | - | 6.01 | 7.1999999999999995E-2 | 8.1000000000000003E-2 | 93.2 | 1 | 2.1000000000000001E-2 | 0.03 | 5.0000000000000001E-3 | - | 7.1 | 14.75 | 60 | 7 min | Alum | 0.05 | 0.5 | 5 | GAC | Anthracite
2022-06-03 06:47:00 AM | 22 | F2 | - | 6.03 | 4.3999999999999997E-2 | 7.2999999999999995E-2 | 91.9 | 1 | 0.02 | 0.03 | 2E-3 | - | 7.5 | 1.47 | 60 | 7 min | Alum | 0.05 | 0.5 | 5 | GAC | Anthracite
2022-06-03 09:41:00 AM | 23 | Raw | - | 5.43 | 0.503 | 0.48799999999999999 | 71.599999999999994 | 29 | - | 7.0000000000000007E-2 | - | - | - | - | 60 | 7 min | Alum | 0 | 0.5 | 5 | GAC | Anthracite
2022-06-03 09:41:00 AM | 23 | Rapid Mix | - | 6.01 | - |  | - | - | - | - | - | - | - | - | 60 | 7 min | Alum | 0 | 0.5 | 5 | GAC | Anthracite
2022-06-03 09:42:00 AM | 23 | DAF | 5.24 | 5.97 | 0.33500000000000002 | 0.38100000000000001 | 86.9 | 9 | - | 0.03 | - | - | - | - | 60 | 7 min | Alum | 0 | 0.5 | 5 | GAC | Anthracite
2022-06-03 09:43:00 AM | 23 | F1 | - | 6.03 | 6.8000000000000005E-2 | 8.1000000000000003E-2 | 92.8 | 0 | - | 0.01 | - | - | 9.6999999999999993 | 14.73 | 60 | 7 min | Alum | 0 | 0.5 | 5 | GAC | Anthracite
2022-06-03 09:44:00 AM | 23 | F2 | - | 5.98 | 3.9E-2 | 8.5999999999999993E-2 | 91.8 | 1 | - | 0.02 | - | - | 10.1 | 1.48 | 60 | 7 min | Alum | 0 | 0.5 | 5 | GAC | Anthracite
2022-06-07 07:05:00 AM | 24 | Raw | - | 5.47 | 0.47199999999999998 | 0.48299999999999998 | 72.099999999999994 | 27 | - | 0.08 | - | - | - | - | 70 | 7 min | Alum | 0 | 0.5 | 5 | GAC | Anthracite
2022-06-07 07:05:00 AM | 24 | Rapid Mix | - | 5.98 | - | 1.77 | - | - | - | - | - | - | - | - | 70 | 7 min | Alum | 0 | 0.5 | 5 | GAC | Anthracite
2022-06-07 07:06:00 AM | 24 | DAF | 5.31 | 6.01 | 0.29499999999999998 | 0.34899999999999998 | 87.7 | 8 | - | 0.04 | - | - | - | - | 70 | 7 min | Alum | 0 | 0.5 | 5 | GAC | Anthracite
2022-06-07 07:07:00 AM | 24 | F1 | - | 5.85 | 6.0999999999999999E-2 | 0.10199999999999999 | 93.9 | 1 | - | 0.03 | - | - | 11.5 | 15 | 70 | 7 min | Alum | 0 | 0.5 | 5 | GAC | Anthracite
2022-06-07 07:08:00 AM | 24 | F2 | - | 5.87 | 3.7999999999999999E-2 | 8.7999999999999995E-2 | 92.5 | 1 | - | 0.03 | - | - | 11.9 | 2.37 | 70 | 7 min | Alum | 0 | 0.5 | 5 | GAC | Anthracite
2022-06-07 10:14:00 AM | 25 | Raw | - | 5.39 | 0.48099999999999998 | 0.54500000000000004 | 71.7 | 28 | 0.22 | 7.0000000000000007E-2 | - | - | - | - | 70 | 7 min | Alum | 0 | 0.5 | 5 | GAC | Anthracite
2022-06-07 10:14:00 AM | 25 | Rapid Mix | - | 6.11 | - | 1.55 | - | - | - | - | - | - | - | - | 70 | 7 min | Alum | 0 | 0.5 | 5 | GAC | Anthracite
2022-06-07 10:16:00 AM | 25 | DAF | 5.31 | 6.02 | 0.27800000000000002 | 0.32800000000000001 | 87 | 8 | 0.16 | 0.04 | - | - | - | - | 70 | 7 min | Alum | 0 | 0.5 | 5 | GAC | Anthracite
2022-06-07 10:17:00 AM | 25 | F1 | - | 5.92 | 7.0999999999999994E-2 | 0.104 | 92.6 | 1 | 0.2 | 0.01 | - | - | 14.6 | 15 | 70 | 7 min | Alum | 0 | 0.5 | 5 | GAC | Anthracite
2022-06-07 10:18:00 AM | 25 | F2 | - | 5.94 | 4.2999999999999997E-2 | 7.4999999999999997E-2 | 90.9 | 1 | 0.15 | 0.02 | - | - | 15 | 2.39 | 70 | 7 min | Alum | 0 | 0.5 | 5 | GAC | Anthracite
2022-06-09 10:31:00 AM | 26 | Raw | - | 5.52 | 0.76 | 0.78300000000000003 | 71.5 | 30 | - | 0.1 | - | - | - | - | 50 | 7 min | Alum | 0 | 0.5 | 5 | GAC | Anthracite
2022-06-09 10:31:00 AM | 26 | Rapid Mix | - | 6.04 | - | 2.0499999999999998 | - | - | - | - | - | - | - | - | 50 | 7 min | Alum | 0 | 0.5 | 5 | GAC | Anthracite
2022-06-09 10:32:00 AM | 26 | DAF | 4.72 | 6.03 | 0.41199999999999998 | 0.55100000000000005 | 86.5 | 12 | - | 0.04 | - | - | - | - | 50 | 7 min | Alum | 0 | 0.5 | 5 | GAC | Anthracite
2022-06-09 10:33:00 AM | 26 | F1 | - | 5.95 | 8.2000000000000003E-2 | 0.129 | 92.8 | 3 | - | 0.01 | - | - | 18.100000000000001 | 15 | 50 | 7 min | Alum | 0 | 0.5 | 5 | GAC | Anthracite
2022-06-09 10:33:59 AM | 26 | F2 | - | 5.92 | 8.5000000000000006E-2 | 0.13900000000000001 | 90.9 | 4 | - | 0.01 | - | - | 18.5 | 2.97 | 50 | 7 min | Alum | 0 | 0.5 | 5 | GAC | Anthracite
2022-06-10 08:59:59 AM | 27 | Raw | - | 5.44 | 0.55400000000000005 | 0.59499999999999997 | 70.599999999999994 | 28 | - | 0.08 | - | - | - | - | 40 | 7 min | Alum | 0 | 0.5 | 5 | GAC | Anthracite | 3.7679999999999998
2022-06-10 08:59:59 AM | 27 | Rapid Mix | - | 6.12 | - | 1.56 | - | - | - | - | - | - | - | - | 40 | 7 min | Alum | 0 | 0.5 | 5 | GAC | Anthracite
2022-06-10 09:01:00 AM | 27 | DAF | 3.34 | 6.07 | 0.70099999999999996 | 0.83599999999999997 | 79.3 | 20 | - | 0.06 | - | - | - | - | 40 | 7 min | Alum | 0 | 0.5 | 5 | GAC | Anthracite | 2.9390000000000001
2022-06-10 09:03:00 AM | 27 | F1 | - | 6.01 | 0.221 | 0.23200000000000001 | 89.5 | 4 | - | 0.03 | - | - | 20.3 | 15 | 40 | 7 min | Alum | 0 | 0.5 | 5 | GAC | Anthracite | 2.0619999999999998
2022-06-10 09:05:00 AM | 27 | F2 | - | 6.03 | 0.151 | 0.184 | 89.7 | 2 | - | 0.03 | - | - | 20.7 | 3.67 | 40 | 7 min | Alum | 0 | 0.5 | 5 | GAC | Anthracite | 2.15
2022-06-13 08:45:00 AM | 28 | Raw | - | 5.43 | 0.61899999999999999 | 0.65200000000000002 | 71.900000000000006 | 29 | - | 0.08 | - | - | - | - | 60 | 23 min | Alum | 0.05 | 0.5 | 5 | GAC | Anthracite
2022-06-13 08:46:00 AM | 28 | Rapid Mix | - | 5.85 | - | 1.82 | - | - | - | - | - | - | - | - | 60 | 23 min | Alum | 0.05 | 0.5 | 5 | GAC | Anthracite
2022-06-13 08:47:00 AM | 28 | DAF | 2.5099999999999998 | 5.78 | 0.16300000000000001 | 0.24399999999999999 | 91 | 4 | - | 0.03 | - | - | - | - | 60 | 23 min | Alum | 0.05 | 0.5 | 5 | GAC | Anthracite
2022-06-13 08:48:00 AM | 28 | F1 | - | 5.79 | 4.7E-2 | 0.108 | 93.6 | 1 | - | 0.03 | - | - | 0.5 | 12.84 | 60 | 23 min | Alum | 0.05 | 0.5 | 5 | GAC | Anthracite
2022-06-13 08:48:00 AM | 28 | F2 | - | 5.82 | 5.2999999999999999E-2 | 0.105 | 93.1 | 1 | - | 0.02 | - | - | 1.1000000000000001 | 1.74 | 60 | 23 min | Alum | 0.05 | 0.5 | 5 | GAC | Anthracite
2022-06-13 10:36:59 AM | 29 | Raw | - | 5.46 | 0.628 | 0.68300000000000005 | 72.3 | 28 | 2.8000000000000001E-2 | 0.08 | - | - | - | - | 60 | 23 min | Alum | 0.05 | 0.5 | 5 | GAC | Anthracite | DBPfp @CWRS
2022-06-13 10:37:59 AM | 29 | Rapid Mix | - | 6.15 | - | 1.73 | - | - | - | - | - | - | - | - | 60 | 23 min | Alum | 0.05 | 0.5 | 5 | GAC | Anthracite
2022-06-13 10:28:00 AM | 29 | DAF | 2.48 | 6.07 | 0.153 | 0.21299999999999999 | 90.8 | 5 | 1.2999999999999999E-2 | 0.03 | - | - | - | - | 60 | 23 min | Alum | 0.05 | 0.5 | 5 | GAC | Anthracite | DBPfp @CWRS
2022-06-13 10:40:00 AM | 29 | F1 | - | 6.01 | 5.1999999999999998E-2 | 0.10299999999999999 | 94.1 | 1 | 1.9E-2 | 0.03 | - | - | 3 | 12.98 | 60 | 23 min | Alum | 0.05 | 0.5 | 5 | GAC | Anthracite | DBPfp @CWRS
2022-06-13 10:41:00 AM | 29 | F2 | - | 6.02 | 5.8000000000000003E-2 | 0.10299999999999999 | 93.2 | 1 | 2.1000000000000001E-2 | 0.03 | - | - | 3.6 | 1.85 | 60 | 23 min | Alum | 0.05 | 0.5 | 5 | GAC | Anthracite | DBPfp @CWRS
2022-06-16 05:14:00 AM | 30 | Raw | - | 5.49 | 0.13 | - | 70.8 | - | - | - | - | - | - | - | 50 | 14 min | Alum | 0 | 10 min | 5 | GAC | Anthracite |  |  | ICP MS Total and dissolved manganese samples @ CWRS
2022-06-16 05:16:00 AM | 30 | Rapid Mix | - | 9.33 | - | - | 70.900000000000006 | - | - | - | - | - | - | - | 50 | 14 min | Alum | 0 | 10 min | 5 | GAC | Anthracite |  |  | ICP MS Total and dissolved manganese samples @ CWRS
2022-06-16 05:14:00 AM | 30 | DAF | 2.21 | 5.65 | 0.45500000000000002 | - | 86.9 | - | - | - | - | - | - | - | 50 | 14 min | Alum | 0 | 10 min | 5 | GAC | Anthracite |  |  | ICP MS Total and dissolved manganese samples @ CWRS
2022-06-16 05:17:00 AM | 30 | F1 | - | 5.61 | 4.1000000000000002E-2 | - | 95.3 | - | 2.4E-2 | - | - | - | 11.5 | 13.96 | 50 | 14 min | Alum | 0 | 10 min | 5 | GAC | Anthracite |  |  | ICP MS Total and dissolved manganese samples @ CWRS
2022-06-16 05:18:00 AM | 30 | F2 | - | 5.63 | 6.0999999999999999E-2 | - | 93.4 | - | 2.1000000000000001E-2 | - | - | - | 12.1 | 3.11 | 50 | 14 min | Alum | 0 | 10 min | 5 | GAC | Anthracite |  |  | ICP MS Total and dissolved manganese samples @ CWRS
2022-06-16 06:04:00 AM | 31 | Raw | - | 5.46 | 0.14000000000000001 | - | 70.900000000000006 | - | - | - | - | - | - | - | 50 | 14 min | Alum | 0.05 | 10 min | 5 | GAC | Anthracite |  |  | ICP MS Total and dissolved manganese samples @ CWRS
2022-06-16 06:05:59 AM | 31 | Rapid Mix | - | 9.52 | - | - | 70.400000000000006 | - | - | - | - | - | - | - | 50 | 14 min | Alum | 0.05 | 10 min | 5 | GAC | Anthracite |  |  | ICP MS Total and dissolved manganese samples @ CWRS
2022-06-16 06:04:00 AM | 31 | DAF | 2.2200000000000002 | 5.71 | 0.44700000000000001 | - | 88.6 | - | - | - | - | - | - | - | 50 | 14 min | Alum | 0.05 | 10 min | 5 | GAC | Anthracite |  |  | ICP MS Total and dissolved manganese samples @ CWRS
2022-06-16 06:05:00 AM | 31 | F1 | - | 5.66 | 4.2000000000000003E-2 | - | 93.9 | - | 0.02 | - | - | - | 12 | 13.98 | 50 | 14 min | Alum | 0.05 | 10 min | 5 | GAC | Anthracite |  |  | ICP MS Total and dissolved manganese samples @ CWRS
2022-06-16 06:05:00 AM | 31 | F2 | - | 5.65 | 5.7000000000000002E-2 | - | 95.2 | - | 1.2999999999999999E-2 | - | - | - | 12.6 | 3.14 | 50 | 14 min | Alum | 0.05 | 10 min | 5 | GAC | Anthracite |  |  | ICP MS Total and dissolved manganese samples @ CWRS
2022-06-16 06:53:00 AM | 32 | Raw | - | 5.41 | 0.13 | - | 72.400000000000006 | - | 2.8000000000000001E-2 | - | - | - | - | - | 50 | 14 min | Alum | 0.1 | 10 min | 5 | GAC | Anthracite |  |  | ICP MS Total and dissolved manganese samples @ CWRS
2022-06-16 06:55:00 AM | 32 | Rapid Mix | - | 9.5399999999999991 | - | - | 70.7 | - | - | - | - | - | - | - | 50 | 14 min | Alum | 0.1 | 10 min | 5 | GAC | Anthracite |  |  | ICP MS Total and dissolved manganese samples @ CWRS
2022-06-16 06:54:00 AM | 32 | DAF | 2.16 | 5.84 | 0.45600000000000002 | - | 88.5 | - | 0.02 | - | - | - | - | - | 50 | 14 min | Alum | 0.1 | 10 min | 5 | GAC | Anthracite |  |  | ICP MS Total and dissolved manganese samples @ CWRS
2022-06-16 06:54:00 AM | 32 | F1 | - | 5.82 | 4.2999999999999997E-2 | - | 93.9 | - | 1.2E-2 | - | - | - | 12.9 | 13.76 | 50 | 14 min | Alum | 0.1 | 10 min | 5 | GAC | Anthracite |  |  | ICP MS Total and dissolved manganese samples @ CWRS
2022-06-16 06:55:00 AM | 32 | F2 | - | 5.79 | 5.6000000000000001E-2 | - | 93.8 | - | 8.0000000000000002E-3 | - | - | - | 13.5 | 3.11 | 50 | 14 min | Alum | 0.1 | 10 min | 5 | GAC | Anthracite
2022-06-16 07:47:00 PM | 33 | Raw | - | 5.49 | 0.14000000000000001 | - | 72.5 | - | - | - | - | - | - | - | 50 | 14 min | Alum | 0.15 | 10 min | 5 | GAC | Anthracite |  |  | ICP MS Total and dissolved manganese samples @ CWRS
2022-06-16 07:49:00 PM | 33 | Rapid Mix | - | 9.58 | - | - | 70.599999999999994 | - | - | - | - | - | - | - | 50 | 14 min | Alum | 0.15 | 10 min | 5 | GAC | Anthracite |  |  | ICP MS Total and dissolved manganese samples @ CWRS
2022-06-16 07:48:00 PM | 33 | DAF | 2.02 | 6.41 | 0.41699999999999998 | - | 87.4 | - | - | - | - | - | - | - | 50 | 14 min | Alum | 0.15 | 10 min | 5 | GAC | Anthracite |  |  | ICP MS Total and dissolved manganese samples @ CWRS
2022-06-16 07:48:00 PM | 33 | F1 | - | 6.24 | 4.2999999999999997E-2 | - | 94.4 | - | 0.01 | - | - | - | 13.8 | 3.6 | 50 | 14 min | Alum | 0.15 | 10 min | 5 | GAC | Anthracite |  |  | ICP MS Total and dissolved manganese samples @ CWRS
2022-06-16 07:48:00 PM | 33 | F2 | - | 6.22 | 6.3E-2 | - | 93.2 | - | 3.0000000000000001E-3 | - | - | - | 14.4 | 2.95 | 50 | 14 min | Alum | 0.15 | 10 min | 5 | GAC | Anthracite |  |  | ICP MS Total and dissolved manganese samples @ CWRS
2022-06-16 08:35:00 AM | 34 | Raw | - | 5.49 | 0.14000000000000001 | - | 72.5 | - | 2.5999999999999999E-2 | - | - | - | - | - | 50 | 14 min | Alum | 0.2 | 10 min | 5 | GAC | Anthracite |  |  | ICP MS Total and dissolved manganese samples @ CWRS
2022-06-16 08:36:00 AM | 34 | Rapid Mix | - | 9.68 | - | - | 70.599999999999994 | - | - | - | - | - | - | - | 50 | 14 min | Alum | 0.2 | 10 min | 5 | GAC | Anthracite |  |  | ICP MS Total and dissolved manganese samples @ CWRS
2022-06-16 08:35:00 AM | 34 | DAF | 1.98 | 6.32 | 0.40400000000000003 | - | 88.3 | - | - | - | - | - | - | - | 50 | 14 min | Alum | 0.2 | 10 min | 5 | GAC | Anthracite |  |  | ICP MS Total and dissolved manganese samples @ CWRS
2022-06-16 08:37:00 AM | 34 | F1 | - | 6.23 | 4.4999999999999998E-2 | - | 93.7 | - | 1.4999999999999999E-2 | - | - | - | 14.6 | 13.51 | 50 | 14 min | Alum | 0.2 | 10 min | 5 | GAC | Anthracite |  |  | ICP MS Total and dissolved manganese samples @ CWRS
2022-06-16 08:38:00 AM | 34 | F2 | - | 6.25 | 6.5000000000000002E-2 | - | 93.5 | - | 8.0000000000000002E-3 | - | - | - | 15 | 2.92 | 50 | 14 min | Alum | 0.2 | 10 min | 5 | GAC | Anthracite |  |  | ICP MS Total and dissolved manganese samples @ CWRS
2022-06-17 05:43:00 AM | 35 | Raw | - | 5.49 | 0.08 | - | 71 | - | 2.8000000000000001E-2 | - | - | - | - | - | 15 | 14 min | Alum | 0 | 10 min | 5 | GAC | Anthracite |  |  | ICP MS Total and dissolved manganese samples @ CWRS
2022-06-17 05:45:00 AM | 35 | Rapid Mix | - | 8.98 | - | - | 71 | - | - | - | - | - | - | - | 15 | 14 min | Alum | 0 | 10 min | 5 | GAC | Anthracite |  |  | ICP MS Total and dissolved manganese samples @ CWRS
2022-06-17 05:43:00 AM | 35 | DAF | 1.96 | 583 | 0.55700000000000005 | - | 85.8 | - | - | - | - | - | - | - | 15 | 14 min | Alum | 0 | 10 min | 5 | GAC | Anthracite |  |  | ICP MS Total and dissolved manganese samples @ CWRS
2022-06-17 05:43:59 AM | 35 | F1 | - | 5.82 | 4.4999999999999998E-2 | - | 94 | - | 2.3E-2 | - | - | - | 15 | 14.59 | 15 | 14 min | Alum | 0 | 10 min | 5 | GAC | Anthracite |  |  | ICP MS Total and dissolved manganese samples @ CWRS
2022-06-17 05:43:59 AM | 35 | F2 | - | 5.84 | 7.0999999999999994E-2 | - | 93.2 | - | 3.6999999999999998E-2 | - | - | - | 15.6 | 3.63 | 15 | 14 min | Alum | 0 | 10 min | 5 | GAC | Anthracite |  |  | ICP MS Total and dissolved manganese samples @ CWRS
2022-06-17 06:41:00 AM | 36 | Raw | - | 5.46 | 0.08 | - | 71.2 | - | - | - | - | - | - | - | 15 | 14 min | Alum | 0.05 | 10 min | 5 | GAC | Anthracite |  |  | ICP MS Total and dissolved manganese samples @ CWRS
2022-06-17 06:44:00 AM | 36 | Rapid Mix | - | 9.11 | - | - | 69.5 | - | - | - | - | - | - | - | 15 | 14 min | Alum | 0.05 | 10 min | 5 | GAC | Anthracite |  |  | ICP MS Total and dissolved manganese samples @ CWRS
2022-06-17 06:41:00 AM | 36 | DAF | 2.12 | 5.96 | 0.57899999999999996 | - | 85.3 | - | - | - | - | - | - | - | 15 | 14 min | Alum | 0.05 | 10 min | 5 | GAC | Anthracite |  |  | ICP MS Total and dissolved manganese samples @ CWRS
2022-06-17 06:42:00 AM | 36 | F1 | - | 5.92 | 5.0999999999999997E-2 | - | 93.3 | - | 2.8000000000000001E-2 | - | - | - | 15.9 | 14.68 | 15 | 14 min | Alum | 0.05 | 10 min | 5 | GAC | Anthracite |  |  | ICP MS Total and dissolved manganese samples @ CWRS
2022-06-17 06:43:00 AM | 36 | F2 | - | 5.89 | 5.8999999999999997E-2 | - | 92.6 | - | 2.1999999999999999E-2 | - | - | - | 16.5 | 3.79 | 15 | 14 min | Alum | 0.05 | 10 min | 5 | GAC | Anthracite |  |  | ICP MS Total and dissolved manganese samples @ CWRS
2022-06-17 07:42:00 AM | 37 | Raw | - | 5.48 | 0.08 | - | 71.7 | - | - | - | - | - | - | - | 15 | 14 min | Alum | 0.1 | 10 min | 5 | GAC | Anthracite |  |  | ICP MS Total and dissolved manganese samples @ CWRS
2022-06-17 07:44:59 AM | 37 | Rapid Mix | - | 9.15 | - | - | 70.3 | - | - | - | - | - | - | - | 15 | 14 min | Alum | 0.1 | 10 min | 5 | GAC | Anthracite |  |  | ICP MS Total and dissolved manganese samples @ CWRS
2022-06-17 07:42:00 AM | 37 | DAF | 2.0299999999999998 | 5.84 | 0.59499999999999997 | - | 84.9 | - | 0.02 | - | - | - | - | - | 15 | 14 min | Alum | 0.1 | 10 min | 5 | GAC | Anthracite |  |  | ICP MS Total and dissolved manganese samples @ CWRS
2022-06-17 07:42:00 AM | 37 | F1 | - | 5.85 | 5.7000000000000002E-2 | - | 93.2 | - | 1.7000000000000001E-2 | - | - | - | 17.100000000000001 | 14.72 | 15 | 14 min | Alum | 0.1 | 10 min | 5 | GAC | Anthracite |  |  | ICP MS Total and dissolved manganese samples @ CWRS
2022-06-17 07:42:59 AM | 37 | F2 | - | 5.86 | 5.8999999999999997E-2 | - | 92.5 | - | 5.0000000000000001E-3 | - | - | - | 17.7 | 3.85 | 15 | 14 min | Alum | 0.1 | 10 min | 5 | GAC | Anthracite |  |  | ICP MS Total and dissolved manganese samples @ CWRS
2022-06-17 08:47:00 AM | 38 | Raw | - | 5.51 | 0.08 | - | 70.8 | - | - | - | - | - | - | - | 15 | 14 min | Alum | 0.15 | 10 min | 5 | GAC | Anthracite |  |  | ICP MS Total and dissolved manganese samples @ CWRS
2022-06-17 08:49:00 AM | 38 | Rapid Mix | - | 9.0399999999999991 | - | - | 70.7 | - | - | - | - | - | - | - | 15 | 14 min | Alum | 0.15 | 10 min | 5 | GAC | Anthracite |  |  | ICP MS Total and dissolved manganese samples @ CWRS
2022-06-17 08:47:00 AM | 38 | DAF | 2.0299999999999998 | 5.78 | 0.61099999999999999 | - | 84.1 | - | - | - | - | - | - | - | 15 | 14 min | Alum | 0.15 | 10 min | 5 | GAC | Anthracite |  |  | ICP MS Total and dissolved manganese samples @ CWRS
2022-06-17 08:48:00 AM | 38 | F1 | - | 5.76 | 5.2999999999999999E-2 | - | 92.6 | - | 1.4999999999999999E-2 | - | - | - | 18.100000000000001 | 14.81 | 15 | 14 min | Alum | 0.15 | 10 min | 5 | GAC | Anthracite |  |  | ICP MS Total and dissolved manganese samples @ CWRS
2022-06-17 08:48:00 AM | 38 | F2 | - | 5.81 | 6.6000000000000003E-2 | - | 92.1 | - | 8.9999999999999993E-3 | - | - | - | 18.7 | 3.88 | 15 | 14 min | Alum | 0.15 | 10 min | 5 | GAC | Anthracite |  |  | ICP MS Total and dissolved manganese samples @ CWRS
2022-06-17 09:44:59 AM | 39 | Raw | - | 5.51 | 0.08 | - | 72 | - | - | - | - | - | - | - | 15 | 14 min | Alum | 0.2 | 10 min | 5 | GAC | Anthracite |  |  | ICP MS Total and dissolved manganese samples @ CWRS
2022-06-17 09:47:00 AM | 39 | Rapid Mix | - | 9.06 | - | - | 70 | - | - | - | - | - | - | - | 15 | 14 min | Alum | 0.2 | 10 min | 5 | GAC | Anthracite |  |  | ICP MS Total and dissolved manganese samples @ CWRS
2022-06-17 09:44:59 AM | 39 | DAF | 2.0299999999999998 | 5.81 | 0.64500000000000002 | - | 85.1 | - | - | - | - | - | - | - | 15 | 14 min | Alum | 0.2 | 10 min | 5 | GAC | Anthracite |  |  | ICP MS Total and dissolved manganese samples @ CWRS
2022-06-17 09:46:00 AM | 39 | F1 | - | 5.83 | 6.0999999999999999E-2 | - | 93.5 | - | 1.4E-2 | - | - | - | 18.100000000000001 | 14.81 | 15 | 14 min | Alum | 0.2 | 10 min | 5 | GAC | Anthracite |  |  | ICP MS Total and dissolved manganese samples @ CWRS
2022-06-17 09:46:00 AM | 39 | F2 | - | 5.85 | 6.6000000000000003E-2 | - | 92.5 | - | 1.0999999999999999E-2 | - | - | - | 18.7 | 3.88 | 15 | 14 min | Alum | 0.2 | 10 min | 5 | GAC | Anthracite |  |  | ICP MS Total and dissolved manganese samples @ CWRS
2022-06-20 08:14:59 AM | 40 | Raw | - | 5.46 | 0.12 | 0.59099999999999997 | 71.7 | 28 | 0.03 | 0.08 | 5.2999999999999999E-2 | - | - | - | 50 | 14 min | Alum | 0.1 | 10 min | 5 | GAC | Anthracite
2022-06-20 08:14:59 AM | 40 | DAF | 2.35 | 5.57 | 0.39500000000000002 | 0.47299999999999998 | 86.9 | 10 | 1.7999999999999999E-2 | 0.04 | 0.32100000000000001 | - | - | - | 50 | 14 min | Alum | 0.1 | 10 min | 5 | GAC | Anthracite
2022-06-20 08:17:00 AM | 40 | F1 | - | 5.55 | 5.3999999999999999E-2 | 0.113 | 94.2 | 4 | 2.9000000000000001E-2 | 0.03 | 1.6E-2 | - | 20.3 | 15 | 50 | 14 min | Alum | 0.1 | 10 min | 5 | GAC | Anthracite
2022-06-20 08:18:00 AM | 40 | F2 | - | 5.53 | 4.2000000000000003E-2 | 0.125 | 92.6 | 2 | 1.2E-2 | 0.02 | 6.0000000000000001E-3 | - | 20.9 | 4.01 | 50 | 14 min | Alum | 0.1 | 10 min | 5 | GAC | Anthracite
2022-06-21 NA | 41 | Raw | - | - | - | - | - | - | 2.5999999999999999E-2 | - | - | - | - | - | 50 | 14 min | Alum | 0.15 | 10 min | 5 | GAC | Anthracite
2022-06-21 NA | 41 | Rapid Mix | - | - | - | - | - | - | - | - | - | - | - | - | 50 | 14 min | Alum | 0.15 | 10 min | 5 | GAC | Anthracite
2022-06-21 NA | 41 | DAF | - | - | - | - | - | - | 0.02 | - | - | - | - | - | 50 | 14 min | Alum | 0.15 | 10 min | 5 | GAC | Anthracite
2022-06-21 NA | 41 | F1 | - | - | - | - | - | - | 1.2E-2 | - | - | - | 2.2999999999999998 | 13.48 | 50 | 14 min | Alum | 0.15 | 10 min | 5 | GAC | Anthracite
2022-06-21 NA | 41 | F2 | - | - | - | - | - | - | 8.9999999999999993E-3 | - | - | - | 2.7 | 3.18 | 50 | 14 min | Alum | 0.15 | 10 min | 5 | GAC | Anthracite
2022-06-22 08:04:00 AM | 42 | Raw | - | 5.57 | 0.09 | 0.57099999999999995 | 71.5 | 28 | 2.4E-2 | 0.08 | 4.2999999999999997E-2 | - | - | - | 50 | 14 min | Alum | 0.05 | 10 min | 5 | GAC | Anthracite
2022-06-22 08:07:00 AM | 42 | Rapid Mix | - | 9.56 | - | - | - | - | - | - | - | - | - | - | 50 | 14 min | Alum | 0.05 | 10 min | 5 | GAC | Anthracite
2022-06-22 08:05:00 PM | 42 | DAF | 2.64 | 6.15 | 0.40200000000000002 | 0.48599999999999999 | 85.9 | 11 | 1.7999999999999999E-2 | 0.04 | 0.29599999999999999 | - | - | - | 50 | 14 min | Alum | 0.05 | 10 min | 5 | GAC | Anthracite
2022-06-22 08:05:00 PM | 42 | F1 | - | 6.05 | 5.2999999999999999E-2 | 0.121 | 91.8 | 1 | 0.01 | 0.03 | 1.2999999999999999E-2 | - | 4.7 | 13.57 | 50 | 14 min | Alum | 0.05 | 10 min | 5 | GAC | Anthracite
2022-06-22 08:06:00 PM | 42 | F2 | - | 6.04 | 4.2999999999999997E-2 | 0.111 | 90.8 | 1 | 1.2E-2 | 0.02 | 2E-3 | - | 5.0999999999999996 | 3.22 | 50 | 14 min | Alum | 0.05 | 10 min | 5 | GAC | Anthracite
2022-06-23 06:12:59 AM | 43 | Raw | - | 5.56 | 0.13 | 0.53400000000000003 | 72.8 | 29 | 2.9000000000000001E-2 | 0.08 | 4.3999999999999997E-2 | - | - | - | 50 | 14 min | Alum | 0.2 | 10 min | 5 | GAC | Anthracite | 5.0529999999999999
2022-06-23 06:14:59 AM | 43 | Rapid Mix | - | 9.52 | - | - | - | - | - | - | - | - | - | - | 50 | 14 min | Alum | 0.2 | 10 min | 5 | GAC | Anthracite
2022-06-23 06:12:59 AM | 43 | DAF | 2.64 | 5.91 | 0.38100000000000001 | 0.47399999999999998 | 87.6 | 10 | 2.3E-2 | 0.04 | 0.31900000000000001 | - | - | - | 50 | 14 min | Alum | 0.2 | 10 min | 5 | GAC | Anthracite | 2.8359999999999999
2022-06-23 06:14:00 AM | 43 | F1 | - | 5.83 | 3.9E-2 | 0.108 | 94.2 | 1 | 5.0000000000000001E-3 | 0.03 | 5.0000000000000001E-3 | - | 10.6 | 14.06 | 50 | 14 min | Alum | 0.2 | 10 min | 5 | GAC | Anthracite | 1.837
2022-06-23 06:14:00 AM | 43 | F2 | - | 5.81 | 0.04 | 0.11799999999999999 | 93.1 | 1 | 6.0000000000000001E-3 | 0.02 | 4.0000000000000001E-3 | - | 11 | 3.51 | 50 | 14 min | Alum | 0.2 | 10 min | 5 | GAC | Anthracite | 2.0760000000000001
2022-06-24 08:42:00 AM | 44 | Raw | - |  | 0.13 | 0.59199999999999997 | 72 | 28 | 0.03 | 0.08 | 4.5999999999999999E-2 | - | - | - | 35 | 14 min | Alum | 0.15 | 10 min | 5 | GAC | Anthracite
2022-06-24 08:43:00 AM | 44 | Rapid Mix | - | 7.86 | - | - | - | - | - | - | - | - | - | - | 35 | 14 min | Alum | 0.15 | 10 min | 5 | GAC | Anthracite
2022-06-24 08:42:00 AM | 44 | DAF | 1.1499999999999999 | 5.15 | 0.624 | 0.76800000000000002 | 83.9 | 16 | 2.4E-2 | 0.04 | 0.35399999999999998 | - | - | - | 35 | 14 min | Alum | 0.15 | 10 min | 5 | GAC | Anthracite
2022-06-24 08:44:00 AM | 44 | F1 | - | 5.51 | 4.2000000000000003E-2 | 0.10199999999999999 | 94.3 | 0 | 1.4999999999999999E-2 | 0.03 | 1.9E-2 | - | 13.7 | 14.12 | 35 | 14 min | Alum | 0.15 | 10 min | 5 | GAC | Anthracite
2022-06-24 08:45:00 AM | 44 | F2 | - | 5.52 | 3.7999999999999999E-2 | 0.109 | 92.8 | 0 | 7.0000000000000001E-3 | 0.03 | 4.0000000000000001E-3 | - | 14.1 | 3.78 | 35 | 14 min | Alum | 0.15 | 10 min | 5 | GAC | Anthracite
2022-06-27 08:09:00 AM | 45 | Raw | - | 5.42 | 0.08 | 0.58699999999999997 | 71.900000000000006 | 28 | - | 0.08 | 4.5999999999999999E-2 | - | - | - | 80 | 7 min | Alum | 0 | 0.5 | 5 | GAC | Anthracite
2022-06-27 08:10:00 AM | 45 | Rapid Mix | - | 6.17 | - | - | - | - | - | - | - | - | - | - | 80 | 7 min | Alum | 0 | 0.5 | 5 | GAC | Anthracite
2022-06-27 08:09:00 AM | 45 | DAF | 2.87 | 6.18 | 0.28899999999999998 | 0.34200000000000003 | 87.9 | 9 | - | 0.04 | 0.36599999999999999 | - | - | - | 80 | 7 min | Alum | 0 | 0.5 | 5 | GAC | Anthracite
2022-06-27 08:10:00 AM | 45 | F1 | - | 6.06 | 4.2000000000000003E-2 | 0.111 | 92.8 | 1 | - | 0.03 | 2.1000000000000001E-2 | - | 18.7 | 14.71 | 80 | 7 min | Alum | 0 | 0.5 | 5 | GAC | Anthracite
2022-06-27 08:10:00 AM | 45 | F2 | - | 6.03 | 3.7999999999999999E-2 | 0.121 | 91.3 | 1 | - | 0.04 | 1.4E-2 | - | 19.100000000000001 | 4.25 | 80 | 7 min | Alum | 0 | 0.5 | 5 | GAC | Anthracite
2022-06-28 06:53:00 AM | 46 | Raw | - | 5.42 | 0.09 | 0.60899999999999999 | 72.099999999999994 | 28 | - | 0.08 | 8.4000000000000005E-2 | - | - | - | 40 | 7 min | Alum | 0 | 0.5 | 5 | GAC | Anthracite
2022-06-28 06:54:00 AM | 46 | Rapid Mix | - | 5.99 | - | 1.56 | - | - | - | - | - | - | - | - | 40 | 7 min | Alum | 0 | 0.5 | 5 | GAC | Anthracite
2022-06-28 06:53:00 AM | 46 | DAF | 2.63 | 5.93 | 0.55200000000000005 | 0.63100000000000001 | 82.3 | 15 | - | 0.04 | 0.30499999999999999 | - | - | - | 40 | 7 min | Alum | 0 | 0.5 | 5 | GAC | Anthracite |  |  | HW benchtop DAF turbidity = 0.579 NTU
2022-06-28 06:55:00 AM | 46 | F1 | - | 5.88 | 5.5E-2 | 0.123 | 92.9 | 1 | - | 0.03 | 3.1E-2 | - | 21.9 | 15 | 40 | 7 min | Alum | 0 | 0.5 | 5 | GAC | Anthracite |  |  | HW benchtop F1 turbidity = 0.077 NTU
2022-06-28 06:56:00 AM | 46 | F2 | - | 5.89 | 4.7E-2 | 0.13100000000000001 | 91.6 | 2 | - | 0.03 | 8.9999999999999993E-3 | - | 22.3 | 4.75 | 40 | 7 min | Alum | 0 | 0.5 | 5 | GAC | Anthracite |  |  | HW benchtop F2 turbidity = 0.080 NTU
2022-06-28 09:31:00 AM | 47 | Raw | - | 5.41 | 0.09 | 0.59799999999999998 | 72.3 | 29 | - | 0.08 | 0.109 | - | - | - | 40 | 7 min | Alum | 0 | 0.5 | 5 | GAC | Anthracite
2022-06-28 09:33:00 AM | 47 | Rapid Mix | - | 6.06 | - | 1.55 | - | - | - | - | - | - | - | - | 40 | 7 min | Alum | 0 | 0.5 | 5 | GAC | Anthracite
2022-06-28 09:31:00 AM | 47 | DAF | 2.74 | 6.02 | 0.748 | 0.82099999999999995 | 78.099999999999994 | 24 | - | 0.05 | 0.38100000000000001 | - | - | - | 40 | 7 min | x | 0 | 0.5 | 5 | GAC | Anthracite
2022-06-28 09:32:00 AM | 47 | F1 | - | 6.01 | 0.18 | 0.24299999999999999 | 90.1 | 7 | - | 0.04 | 0.17399999999999999 | - | 24.8 | 15 | 40 | 7 min | Alum | 0 | 0.5 | 5 | GAC | Anthracite
2022-06-28 09:32:00 AM | 47 | F2 | - | 6.02 | 9.4E-2 | 0.17399999999999999 | 90 | 5 | - | 0.03 | 0.10199999999999999 | - | 25.2 | 5.41 | 40 | 7 min | Alum | 0 | 0.5 | 5 | GAC | Anthracite
2022-06-29 08:28:00 AM | 48 | Raw | - | 5.34 | 0.13 | 0.59899999999999998 | 72.7 | 27 | - | 0.08 | 6.8000000000000005E-2 | - | - | - | 50 | 7 min | Alum | 0 | 0.5 | 5 | GAC | Anthracite
2022-06-29 08:28:59 AM | 48 | Rapid Mix | - | 5.86 | - | - | - | - | - | - | - | - | - | - | 50 | 7 min | Alum | 0 | 0.5 | 5 | GAC | Anthracite
2022-06-29 08:28:00 AM | 48 | DAF | 1.91 | 5.77 | 0.39500000000000002 | 0.497 | 86.3 | 11 | - | 0.02 | 0.32200000000000001 | - | - | - | 50 | 7 min | Alum | 0 | 0.5 | 5 | GAC | Anthracite
2022-06-29 08:30:00 AM | 48 | F1 | - | 5.74 | 0.19800000000000001 | 0.26600000000000001 | 90.6 | 4 | - | 0.03 | 0.17599999999999999 | - | 27 | 15 | 50 | 7 min | Alum | 0 | 0.5 | 5 | GAC | Anthracite
2022-06-29 08:31:00 AM | 48 | F2 | - | 5.76 | 0.108 | 0.189 | 90.9 | 2 | - | 0.03 | 0.108 | - | 27.4 | 6.09 | 50 | 7 min | Alum | 0 | 0.5 | 5 | GAC | Anthracite
2022-06-30 06:56:00 AM | 49 | Raw | - | 5.76 | 0.08 | - | 70.900000000000006 | 28 | - | 0.08 | 6.8000000000000005E-2 | - | - | - | 50 | 7 min | Alum | 0 | 0.5 | 5 | GAC | Anthracite
2022-06-30 06:56:00 AM | 49 | Rapid Mix | - | 5.87 | - | - | - | - | - | - | - | - | - | - | 50 | 7 min | Alum | 0 | 0.5 | 5 | GAC | Anthracite
2022-06-30 06:57:00 AM | 49 | DAF | 2.14 | - | 0.52800000000000002 | 0.63300000000000001 | 84.5 | 15 | - | 0.04 | 0.27300000000000002 | - | - | - | 50 | 7 min | Alum | 0 | 0.5 | 5 | GAC | Anthracite
2022-06-30 06:57:00 AM | 49 | F1 | - | - | 0.19400000000000001 | 0.17599999999999999 | 92.6 | 2 | - | 0.03 | 0.114 | - | 29.9 | 15 | 50 | 7 min | Alum | 0 | 0.5 | 5 | GAC | Anthracite
2022-06-30 06:57:00 AM | 49 | F2 | - | - | 0.124 | 0.16500000000000001 | 91.5 | 2 | - | - | - | - | 30.3 | 6.74 | 50 | 7 min | Alum | 0 | 0.5 | 5 | GAC | Anthracite
2022-07-04 05:29:59 AM | 49 | DAF | 3.16 | 6.74 | - | - | - | - | - | - | - | - | - | - | 50 | 7 min | Alum | 0 | 0.5 | 5 | GAC | Anthracite
2022-07-04 06:20:00 AM | 49 | DAF | 3.05 | 6.57 | - | - | - | - | - | - | - | - | - | - | 50 | 7 min | Alum | 0 | 0.5 | 5 | GAC | Anthracite
2022-07-04 07:28:00 AM | 50 | Raw | - | 5.66 | - | 0.53400000000000003 | 73 | 27 | - | - | 4.1000000000000002E-2 | - | - | - | 50 | 7 min | Alum | 0 | 0.5 | 5 | GAC | Anthracite
2022-07-04 07:23:00 AM | 50 | Rapid Mix | - | 6.55 | - | 1.71 | - | - | - | - | - | - | - | - | 50 | 7 min | Alum | 0 | 0.5 | 5 | GAC | Anthracite
2022-07-04 07:26:00 AM | 50 | DAF | 2.89 | 6.58 | 0.623 | 0.67100000000000004 | 82.9 | 15 | - | - | 0.36499999999999999 | - | - | - | 50 | 7 min | Alum | 0 | 0.5 | 5 | GAC | Anthracite
2022-07-04 07:30:00 AM | 50 | F1 | - | 6 | 6.9000000000000006E-2 | 0.124 | 93.7 | 1 | - | - | 2.5999999999999999E-2 | - | 0.8 | 12.66 | 50 | 7 min | Alum | 0 | 0.5 | 5 | GAC | Anthracite
2022-07-04 07:32:00 AM | 50 | F2 | - | 6.28 | 6.8000000000000005E-2 | 0.126 | 91 | 2 | - | - | 2.9000000000000001E-2 | - | 1.2 | 2.93 | 50 | 7 min | Alum | 0 | 0.5 | 5 | GAC | Anthracite
2022-07-04 09:11:59 AM | 51 | Raw | - | 5.68 | - | 0.53900000000000003 | 72.7 | 25 | - | - | - | - | - | - | 50 | 7 min | Alum | 0 | 0.5 | 5 | GAC | Anthracite
2022-07-04 09:07:59 AM | 51 | Rapid Mix | - | 6.44 | - | 1.91 | - | - | - | - | - | - | - | - | 50 | 7 min | Alum | 0 | 0.5 | 5 | GAC | Anthracite
2022-07-04 09:10:00 AM | 51 | DAF | 2.56 | 6.36 | 0.53200000000000003 | 0.61 | 83.3 | 11 | - | - | 0.29699999999999999 | - | - | - | 50 | 7 min | Alum | 0 | 0.5 | 5 | GAC | Anthracite
2022-07-04 09:13:00 AM | 51 | F1 | - | 6.01 | 5.7000000000000002E-2 | 0.106 | 92.7 | 1 | - | - | 2.7E-2 | - | 2.6 | 12.7 | 50 | 7 min | Alum | 0 | 0.5 | 5 | GAC | Anthracite
2022-07-04 09:13:59 AM | 51 | F2 | - | 6.29 | 5.2999999999999999E-2 | 0.121 | 91.1 | 1 | - | - | 2.3E-2 | - | 3 | 3.01 | 50 | 7 min | Alum | 0 | 0.5 | 5 | GAC | Anthracite
2022-07-06 05:41:59 AM | 52 | Raw | - | 5.5 | - | 0.51600000000000001 | 72.900000000000006 | 28 | - | - | 5.2999999999999999E-2 | - | - | - | 90 | 7 min | Alum | 0 | 0.5 | 5 | GAC | Anthracite
2022-07-06 05:38:00 AM | 52 | Rapid Mix | - | 6.86 | - | 1.46 | - | - | - | - | - | - | - | - | 90 | 7 min | Alum | 0 | 0.5 | 5 | GAC | Anthracite
2022-07-06 05:39:59 AM | 52 | DAF | 3.78 | 6.82 | 0.27600000000000002 | 0.35099999999999998 | 87.6 | 9 | - | - | 0.34300000000000003 | - | - | - | 90 | 7 min | Alum | 0 | 0.5 | 5 | GAC | Anthracite
2022-07-06 05:43:00 AM | 52 | F1 | - | 6.03 | 4.2000000000000003E-2 | 9.7000000000000003E-2 | 93.4 | 1 | - | - | 6.0000000000000001E-3 | - | 4.2 | 13.6 | 90 | 7 min | Alum | 0 | 0.5 | 5 | GAC | Anthracite
2022-07-06 05:45:00 AM | 52 | F2 | - | 6.27 | 0.04 | 0.104 | 91.7 | 2 | - | - | 1.2999999999999999E-2 | - | 4.5999999999999996 | 3.58 | 90 | 7 min | Alum | 0 | 0.5 | 5 | GAC | Anthracite
2022-07-06 07:56:59 AM | 53 | Raw | - | 5.55 | - | 0.54500000000000004 | 73 | 28 | - | - | - | - | - | - | 90 | 7 min | Alum | 0 | 0.5 | 5 | GAC | Anthracite
2022-07-06 07:54:00 AM | 53 | Rapid Mix | - | 6.54 | - | 1.55 | - | - | - | - | - | - | - | - | 90 | 7 min | Alum | 0 | 0.5 | 5 | GAC | Anthracite
2022-07-06 07:56:00 AM | 53 | DAF | 3.46 | 6.53 | 0.249 | 0.35399999999999998 | 88.1 | 9 | - | - | 0.373 | - | - | - | 90 | 7 min | Alum | 0 | 0.5 | 5 | GAC | Anthracite
2022-07-06 07:58:59 AM | 53 | F1 | - | 6.23 | 4.4999999999999998E-2 | 9.8000000000000004E-2 | 93.3 | 2 | - | - | 1.7999999999999999E-2 | - | 6.5 | 13.87 | 90 | 7 min | Alum | 0 | 0.5 | 5 | GAC | Anthracite
2022-07-06 08:00:00 AM | 53 | F2 | - | 6.43 | 3.3000000000000002E-2 | 0.109 | 92.3 | 4 | - | - | 3.7999999999999999E-2 | - | 6.9 | 3.78 | 90 | 7 min | Alum | 0 | 0.5 | 5 | GAC | Anthracite
2022-07-06 10:08:00 AM | 54 | Raw | - | 5.55 | - | 0.52300000000000002 | 73 | 27 | - | - | - | - | - | - | 100 | 7 min | Alum | 0 | 0.5 | 5 | GAC | Anthracite
2022-07-06 10:06:00 AM | 54 | Rapid Mix | - | 6.71 | - | 1.66 | - | - | - | - | - | - | - | - | 100 | 7 min | Alum | 0 | 0.5 | 5 | GAC | Anthracite
2022-07-06 10:07:00 AM | 54 | DAF | 3.2 | 6.7 | 0.26200000000000001 | 0.33600000000000002 | 88.5 | 8 | - | - | 0.28999999999999998 | - | - | - | 100 | 7 min | Alum | 0 | 0.5 | 5 | GAC | Anthracite
2022-07-06 10:09:00 AM | 54 | F1 | - | 6.23 | 0.05 | 9.5000000000000001E-2 | 92.8 | 1 | - | - | 1.7999999999999999E-2 | - | 8.6 | 14.3 | 100 | 7 min | Alum | 0 | 0.5 | 5 | GAC | Anthracite
2022-07-06 10:10:00 AM | 54 | F2 | - | 6.53 | 3.4000000000000002E-2 | 9.5000000000000001E-2 | 92.1 | 1 | - | - | 1.2E-2 | - | 9 | 4.07 | 100 | 7 min | Alum | 0 | 0.5 | 5 | GAC | Anthracite
2022-07-07 07:40:00 AM | 55 | Raw | - | 4.49 | - | - | - | - | - | - | - | - | - | - | 40 | 7 min | Alum | 0 | 0.5 | 5 | GAC | Anthracite
2022-07-07 07:40:00 AM | 55 | DAF | - | 4.75 | - | - | - | - | - | - | - | - | - | - | 40 | 7 min | Alum | 0 | 0.5 | 5 | GAC | Anthracite
2022-07-07 07:50:00 AM | 56 | Raw | - | 4.5 | - | - | - | - | - | - | - | - | - | - | 40 | 7 min | Alum | 0 | 0.5 | 5 | GAC | Anthracite
2022-07-07 07:50:00 AM | 56 | DAF | - | 6.2 | - | - | - | - | - | - | - | - | - | - | 40 | 7 min | Alum | 0 | 0.5 | 5 | GAC | Anthracite
2022-07-07 08:16:00 AM | 56 | DAF | - | 5.65 | - | - | - | - | - | - | - | - | - | - | 40 | 7 min | Alum | 0 | 0.5 | 5 | GAC | Anthracite
2022-07-07 09:15:00 AM | 56 | DAF | - | 5.9 | - | - | - | - | - | - | - | - | - | - | 40 | 7 min | Alum | 0 | 0.5 | 5 | GAC | Anthracite
2022-07-07 10:03:00 AM | 56 | DAF |  | 5.67 | - | - | - | - | - | - | - | - | - | - | 50 | 7 min | Alum | 0 | 0.5 | 5 | GAC | Anthracite
2022-07-07 10:54:00 AM | 56 | DAF | - | 6.42 | - | - | - | - | - | - | - | - | - | - | 50 | 7 min | Alum | 0 | 0.5 | 5 | GAC | Anthracite
2022-07-08 04:34:00 AM | 56 | DAF | - | 6.26 | 1.2010000000000001 | - | - | - | - | - | - | - | - | - | 50 | 7 min | Alum | 0 | 0.5 | 5 | GAC | Anthracite
2022-07-08 04:48:00 AM | 56 | DAF | - | 6.28 | 1.002 | - | - | - | - | - | - | - | - | - | 50 | 7 min | Alum | 0 | 0.5 | 5 | GAC | Anthracite
2022-07-08 05:03:00 AM | 56 | DAF | - | 6.43 | 0.76400000000000001 | - | - | - | - | - | - | - | - | - | 50 | 7 min | Alum | 0 | 0.5 | 5 | GAC | Anthracite
2022-07-08 05:20:00 AM | 56 | DAF | - | 6.42 | 0.71899999999999997 | - | - | - | - | - | - | - | - | - | 50 | 7 min | Alum | 0 | 0.5 | 5 | GAC | Anthracite
2022-07-08 06:00:00 AM | 57 | Raw | - | 5.5 | 0.06 | 0.56299999999999994 | 73.099999999999994 | 28 | - | 7.0000000000000007E-2 | 2.5000000000000001E-2 | - | - | - | 50 | 7 min | Alum | 0 | 0.5 | 5 | GAC | Anthracite
2022-07-08 06:01:00 AM | 57 | Rapid Mix | - | 6.41 | - | - | - | - | - | - | - | - | - | - | 50 | 7 min | Alum | 0 | 0.5 | 5 | GAC | Anthracite
2022-07-08 06:01:00 AM | 57 | DAF | - | 6.33 | 0.67 | 0.76 | 80.599999999999994 | 17 | - | 0.04 | 4.1000000000000002E-2 | - | - | - | 50 | 7 min | Alum | 0 | 0.5 | 5 | GAC | Anthracite
2022-07-08 06:05:00 AM | 57 | F1 | - | 6.11 | 8.3000000000000004E-2 | 0.104 | 94.1 | 1 | - | 0.03 | 3.1E-2 | - | - | 15 | 50 | 7 min | Alum | 0 | 0.5 | 5 | GAC | Anthracite
2022-07-08 06:05:59 AM | 57 | F2 | - | 6.21 | 5.2999999999999999E-2 | 0.105 | 92.5 | 2 | - | 0.02 | 0.04 | - | - | 5.5 | 50 | 7 min | Alum | 0 | 0.5 | 5 | GAC | Anthracite
2022-07-08 07:18:00 AM | 57 | DAF | - | 6.52 | 0.998 | - | - | - | - | - | - | - | - | - | 50 | 7 min | Alum | 0 | 0.5 | 5 | GAC | Anthracite
2022-07-08 08:16:00 AM | 57 | DAF | - | - | 0.86 | - | - | - | - | - | - | - | - | - | 50 | 7 min | Alum | 0 | 0.5 | 5 | GAC | Anthracite
2022-07-08 08:16:00 AM | 57 | Rapid Mix | - | 6.58 | - | - | - | - | - | - | - | - | - | - | 50 | 7 min | Alum | 0 | 0.5 | 5 | GAC | Anthracite
2022-07-08 09:03:00 AM | 57 | DAF | - | - | 0.629 | - | - | - | - | - | - | - | - | - | 50 | 7 min | Alum | 0 | 0.5 | 5 | GAC | Anthracite
2022-07-08 09:03:00 AM | 57 | Rapid Mix | - | 6.22 | - | - | - | - | - | - | - | - | - | - | 50 | 7 min | Alum | 0 | 0.5 | 5 | GAC | Anthracite
2022-07-08 09:33:00 AM | 57 | DAF | 6.56 | 6.38 | 0.57399999999999995 | - | - | - | - | - | - | - | - | - | 50 | 7 min | Alum | 0 | 0.5 | 5 | GAC | Anthracite
2022-07-08 09:40:00 AM | 57 | Rapid Mix | - | 6.42 | - | - | - | - | - | - | - | - | - | - | 50 | 7 min | Alum | 0 | 0.5 | 5 | GAC | Anthracite
2022-07-08 10:48:00 AM | 57 | DAF | 6.48 | 6.33 | 0.52600000000000002 | - | - | - | - | - | - | - | - | - | 50 | 7 min | Alum | 0 | 0.5 | 5 | GAC | Anthracite
2022-07-08 10:54:00 AM | 57 | Rapid Mix | - | 6.35 | - | - | - | - | - | - | - | - | - | - | 50 | 7 min | Alum | 0 | 0.5 | 5 | GAC | Anthracite
2022-07-11 05:07:00 AM | 57 | DAF | 6.55 | 6.23 | 0.46400000000000002 | - | - | - | - | - | - | - | - | - | 50 | 7 min | Alum | 0 | 0.5 | 5 | GAC | Anthracite
2022-07-11 05:39:59 AM | 57 | DAF | 6.38 | 6.2 | 0.46200000000000002 | - | - | - | - | - | - | - | - | - | 50 | 7 min | Alum | 0 | 0.5 | 5 | GAC | Anthracite
2022-07-11 07:25:00 AM | 58 | Raw | - | 5.56 | 0.09 | 0.51200000000000001 | 73.5 | 24 | - | 0.06 | 6.6000000000000003E-2 | - | - | - | 50 | 7 min | Alum | 0 | 0.5 | 5 | GAC | Anthracite
2022-07-11 07:26:00 AM | 58 | Rapid Mix | - | 6.31 | - | - | - | - | - | - | - | - | - | - | 50 | 7 min | Alum | 0 | 0.5 | 5 | GAC | Anthracite
2022-07-11 07:25:00 AM | 58 | DAF | 5.9 | 6.23 | 0.44500000000000001 | 0.51 | 84.2 | 12 | - | 0.04 | 0.35299999999999998 | - | - | - | 50 | 7 min | Alum | 0 | 0.5 | 5 | GAC | Anthracite
2022-07-11 07:28:00 AM | 58 | F1 | - | 6.11 | 0.06 | 0.113 | 92.1 | 1 | - | 0.01 | 2.3E-2 | - | - | 12.43 | 50 | 7 min | Alum | 0 | 0.5 | 5 | GAC | Anthracite
2022-07-11 07:28:00 AM | 58 | F2 | - | 6.22 | 4.7E-2 | 0.10100000000000001 | 91.4 | 1 | - | 0.02 | 2.4E-2 | - | - | 3.25 | 50 | 7 min | Alum | 0 | 0.5 | 5 | GAC | Anthracite
2022-07-11 09:38:00 AM | 58 | Rapid Mix | - | 6.26 | - | - | - | - | - | - | - | - | - | - | 50 | 7 min | Alum | 0 | 0.5 | 5 | GAC | Anthracite
2022-07-11 09:38:00 AM | 58 | DAF | 5.49 | 6.22 | 0.41699999999999998 | - | - | - | - | - | - | - | - | - | 50 | 7 min | Alum | 0 | 0.5 | 5 | GAC | Anthracite
2022-07-11 09:38:00 AM | 58 | F1 | - | - | 5.0999999999999997E-2 | - | - | - | - | - | - | - | - | 12.46 | 50 | 7 min | Alum | 0 | 0.5 | 5 | GAC | Anthracite
2022-07-11 09:38:00 AM | 58 | F2 | - | - | 4.1000000000000002E-2 | - | - | - | - | - | - | - | - | 3.21 | 50 | 7 min | Alum | 0 | 0.5 | 5 | GAC | Anthracite
2022-07-11 10:37:59 AM | 58 | DAF | 5.41 | 6.31 | 0.42799999999999999 | - | - | - | - | - | - | - | - |  | 50 | 7 min | Alum | 0.3 | 0.5 | 5 | GAC | Anthracite
2022-07-11 10:37:59 AM | 58 | F1 | - | - | 4.9000000000000002E-2 | - | - | - | - | - | - | - | - | 12.51 | 50 | 7 min | Alum | 0.3 | 0.5 | 5 | GAC | Anthracite
2022-07-11 10:37:59 AM | 58 | F2 | - | - | 4.1000000000000002E-2 | - | - | - | - | - | - | - | - | 3.2 | 50 | 7 min | Alum | 0.3 | 0.5 | 5 | GAC | Anthracite
2022-07-12 07:05:00 AM | 58 | DAF | 5.84 | - | 0.50600000000000001 | - | - | - | - | - | - | - | - | - | 50 | 7 min | Alum | 0.15 | 0.5 | 5 | GAC | Anthracite
2022-07-12 07:44:59 AM | 59 | Raw | - | 5.49 |  | 0.55600000000000005 | 73.3 | 23 | - | 0.08 | 4.2000000000000003E-2 | - | - | - | 50 | 7 min | Alum | 0.15 | 0.5 | 5 | GAC | Anthracite
2022-07-12 07:44:59 AM | 59 | Rapid Mix | - | 6.19 | - | - | - | - | - | - | - | - | - | - | 50 | 7 min | Alum | 0.15 | 0.5 | 5 | GAC | Anthracite
2022-07-12 07:44:59 AM | 59 | DAF | 6.76 | 6.21 | 0.41099999999999998 | 0.53100000000000003 | 85.1 | 10 | - | 0.03 | 0.14199999999999999 | - | - | - | 50 | 7 min | Alum | 0.15 | 0.5 | 5 | GAC | Anthracite
2022-07-12 07:44:59 AM | 59 | F1 | - | 6.16 | 4.4999999999999998E-2 | 0.10100000000000001 | 93.3 | 1 | - | 0.03 | 1.2999999999999999E-2 | - | - | 13.34 | 50 | 7 min | Alum | 0.15 | 0.5 | 5 | GAC | Anthracite
2022-07-12 07:44:59 AM | 59 | F2 | - | 6.19 | 3.7999999999999999E-2 | 9.8000000000000004E-2 | 92.3 | 0 | - | 0.03 | 1.2999999999999999E-2 | - | - | 3.56 | 50 | 7 min | Alum | 0.15 | 0.5 | 5 | GAC | Anthracite
2022-07-12 11:20:00 AM | 59 | DAF | 6.79 | 6.45 | 0.39400000000000002 | - | - | - | - | - | - | - | - | - | 50 | 7 min | Alum | 0.15 | 0.5 | 5 | GAC | Anthracite
2022-07-12 11:20:00 AM | 59 | F1 | - | - | 4.4999999999999998E-2 | - | - | - | - | - | - | - | - | 13.29 | 50 | 7 min | Alum | 0.15 | 0.5 | 5 | GAC | Anthracite
2022-07-12 11:20:00 AM | 59 | F2 | - | - | 3.6999999999999998E-2 | - | - | - | - | - | - | - | - | 3.59 | 50 | 7 min | Alum | 0.15 | 0.5 | 5 | GAC | Anthracite
2022-07-12 12:25:00 PM | 59 | DAF | 6.63 | 6.28 | 0.39400000000000002 | - | - | - | - | - | - | - | - | - | 50 | 7 min | Alum | 0.15 | 0.5 | 5 | GAC | Anthracite
2022-07-12 12:25:00 PM | 59 | F1 | - | - | 4.4999999999999998E-2 | - | - | - | - | - | - | - | - | 13.49 | 50 | 7 min | Alum | 0.15 | 0.5 | 5 | GAC | Anthracite
2022-07-12 12:25:00 PM | 59 | F2 | - | - | 3.5000000000000003E-2 | - | - | - | - | - | - | - | - | 3.79 | 50 | 7 min | Alum | 0.15 | 0.5 | 5 | GAC | Anthracite
2022-07-13 05:37:00 AM | 59 | DAF | - | 6.3 | 0.40300000000000002 | - | - | - | - | - | - | - | - | - | 50 | 7 min | Alum | 0.15 | 0.5 | 5 | GAC | Anthracite
2022-07-13 06:46:00 AM | 59 | DAF | 6.78 | 6.13 | 0.38600000000000001 | - | - | - | - | - | - | - | - | - | 50 | 7 min | Alum | 0.15 | 0.5 | 5 | GAC | Anthracite
2022-07-13 07:32:00 AM | 60 | Raw | - | 5.63 |  | - | - | - | - | - | - | - | - | - | 50 | 7 min | Alum | 0.15 | 0.5 | 5 | GAC | Anthracite
2022-07-13 07:32:00 AM | 60 | DAF | - | 6.01 | 0.374 | - | - | - | - | - | - | - | - | - | 50 | 7 min | Alum | 0.15 | 0.5 | 5 | GAC | Anthracite
2022-07-13 08:33:00 AM | 60 | DAF | 5.96 | 5.99 | 0.36299999999999999 | - | - | - | - | - | - | - | - | - | 50 | 7 min | Alum | 0.15 | 0.5 | 5 | GAC | Anthracite
2022-07-13 09:47:00 AM | 61 | Raw | - | 5.49 | 0.439 | 0.46400000000000002 | 74.2 | 42 | - | 0.06 | 0.05 | - | - | - | 50 | 7 min | Alum | 0.15 | 0.5 | 5 | GAC | Anthracite
2022-07-13 09:47:00 AM | 61 | Rapid Mix | - |  | - | - | - | - | - | - | - | - | - | - | 50 | 7 min | Alum | 0.15 | 0.5 | 5 | GAC | Anthracite
2022-07-13 09:47:00 AM | 61 | DAF | 6.71 | 6.03 | 0.372 | 0.51500000000000001 | 85.7 | 17 | - | 0.04 | 0.309 | - | - | - | 50 | 7 min | Alum | 0.15 | 0.5 | 5 | GAC | Anthracite
2022-07-13 09:48:59 AM | 61 | F1 | - | 6.02 | 4.5999999999999999E-2 | 0.13600000000000001 | 93.9 | 1 | - | 0.01 | 3.0000000000000001E-3 | - | - | 15 | 50 | 7 min | Alum | 0.15 | 0.5 | 5 | GAC | Anthracite
2022-07-13 09:50:00 AM | 61 | F2 | - | 6.02 | 3.4000000000000002E-2 | 0.12 | 93.4 | 0 | - | 0.03 | 1.0999999999999999E-2 | - | - | 4.0599999999999996 | 50 | 7 min | Alum | 0.15 | 0.5 | 5 | GAC | Anthracite
2022-07-14 04:54:59 AM | 62 | Raw | - | 5.57 | 0.43099999999999999 | - | - | - | - | - | - | - | - | - | 50 | 7 min | Alum | 0.15 | 0.5 | 5 | GAC | Anthracite
2022-07-14 05:10:00 AM | 62 | DAF | - | 6.05 | 0.44400000000000001 | - | - | - | - | - | - | - | - | - | 50 | 7 min | Alum | 0.15 | 0.5 | 5 | GAC | Anthracite
2022-07-14 05:10:00 AM | 62 | Rapid Mix | - | 6.05 | - | - | - | - | - | - | - | - | - | - | 50 | 7 min | Alum | 0.15 | 0.5 | 5 | GAC | Anthracite
2022-07-14 05:59:00 AM | 62 | DAF | - | 6.05 | 0.371 | - | - | - | - | - | - | - | - | - | 50 | 7 min | Alum | 0.15 | 0.5 | 5 | GAC | Anthracite
2022-07-14 06:52:00 AM | 62 | DAF | - | 6.05 | 0.36399999999999999 | - | - | - | - | - | - | - | - | - | 50 | 7 min | Alum | 0.15 | 0.5 | 5 | GAC | Anthracite
2022-07-14 07:28:00 AM | 63 | Raw | - | 5.56 | 0.44800000000000001 | 0.50900000000000001 | 74.5 | 29 | - | 0.1 | 5.2999999999999999E-2 | - | - | - | 50 | 7 min | Alum | 0.15 | 0.5 | 5 | GAC | Anthracite
2022-07-14 07:28:00 AM | 63 | Rapid Mix | - | 6.05 | - | - | - | - | - | - | - | - | - | - | 50 | 7 min | Alum | 0.15 | 0.5 | 5 | GAC | Anthracite
2022-07-14 07:28:00 AM | 63 | DAF | - | 6.02 | 0.36299999999999999 | 0.46100000000000002 | 87.2 | 12 | - | 0.04 | 0.223 | - | - | - | 50 | 7 min | Alum | 0.15 | 0.5 | 5 | GAC | Anthracite
2022-07-14 07:30:00 AM | 63 | F1 | - | 6.03 | 4.3999999999999997E-2 | 0.112 | 93.5 | 2 | - | 0.04 | 3.2000000000000001E-2 | - | - | 15 | 50 | 7 min | Alum | 0.15 | 0.5 | 5 | GAC | Anthracite
2022-07-14 07:30:00 AM | 63 | F2 | - | 6.05 | 3.5999999999999997E-2 | 0.10100000000000001 | 93.3 | 3 | - | 0.03 | 2.7E-2 | - | - | 4.0599999999999996 | 50 | 7 min | Alum | 0.15 | 0.5 | 5 | GAC | Anthracite
2022-07-14 09:03:00 AM | 63 | DAF | 6.32 | 6.16 | 0.36 | - | - | - | - | - | - | - | - | - | 50 | 7 min | Alum | 0.15 | 0.5 | 5 | GAC | Anthracite
2022-07-14 09:03:00 AM | 63 | F1 | - | - | 4.2999999999999997E-2 | - | - | - | - | - | - | - | - | 11.99 | 50 | 7 min | Alum | 0.15 | 0.5 | 5 | GAC | Anthracite
2022-07-14 09:03:00 AM | 63 | F2 | - | - | 3.5999999999999997E-2 | - | - | - | - | - | - | - | - | 2.66 | 50 | 7 min | Alum | 0.15 | 0.5 | 5 | GAC | Anthracite
2022-07-15 05:26:00 AM | 63 | RAW | - | - | 0.40300000000000002 | - | - | - | - | - | - | - | - | - | 50 | 7 min | Alum | 0.15 | 0.5 | 5 | GAC | Anthracite
2022-07-15 05:26:00 AM | 63 | DAF | 6.08 | 5.96 | 0.34399999999999997 | - | - | - | - | - | - | - | - | - | 50 | 7 min | Alum | 0.15 | 0.5 | 5 | GAC | Anthracite
2022-07-15 07:25:00 AM | 64 | Raw | - | 6.01 | 0.39300000000000002 | 0.52600000000000002 | 76 | 26 | - | 0.06 | 4.5999999999999999E-2 | - | - | - | 50 | 7 min | Alum | 0.1 | 0.5 | 5 | GAC | Anthracite
2022-07-15 07:25:00 AM | 64 | Rapid Mix | - | 6.38 | - | - | - | - | - | - | - | - | - | - | 50 | 7 min | Alum | 0.1 | 0.5 | 5 | GAC | Anthracite
2022-07-15 07:25:00 AM | 64 | DAF | 6.1 | 6.34 | 0.36299999999999999 | 0.437 | 87.9 | 11 | - | 0.04 | 0.33200000000000002 | - | - | - | 50 | 7 min | Alum | 0.1 | 0.5 | 5 | GAC | Anthracite
2022-07-15 07:25:00 AM | 64 | F1 | - | 6.3 | 4.8000000000000001E-2 | 0.11 | 93.9 | 3 | - | 0.03 | 3.2000000000000001E-2 | - | - | 12.44 | 50 | 7 min | Alum | 0.1 | 0.5 | 5 | GAC | Anthracite
2022-07-15 07:25:00 AM | 64 | F2 | - | 6.15 | 3.5000000000000003E-2 | 0.11600000000000001 | 92.9 | 3 | - | 0.01 | 1.4E-2 | - | - | 3.43 | 50 | 7 min | Alum | 0.1 | 0.5 | 5 | GAC | Anthracite
2022-07-15 11:10:00 AM | 64 | DAF | 6.12 | - | 0.38 | - | - | - | - | - | - | - | - |  | 50 | 7 min | Alum | 0.1 | 0.5 | 5 | GAC | Anthracite
2022-07-15 11:10:00 AM | 64 | F1 | - | - | 4.2000000000000003E-2 | - | - | - | - | - | - | - | - | 12.24 | 50 | 7 min | Alum | 0.1 | 0.5 | 5 | GAC | Anthracite
2022-07-15 11:10:00 AM | 64 | F2 | - | - | 3.4000000000000002E-2 | - | - | - | - | - | - | - | - | 3.53 | 50 | 7 min | Alum | 0.1 | 0.5 | 5 | GAC | Anthracite
2022-07-18 07:16:00 AM | 65 | Raw | - | 5.63 | 0.39600000000000002 | 0.442 | 72.8 | 28 | - | 0.08 | 5.2999999999999999E-2 | - | - | - | 60 | 7 min | Alum | 0 | 0.5 | 5 | GAC | Anthracite
2022-07-18 07:16:00 AM | 65 | Rapid Mix | - | 5.91 | - | 1.47 | - | - | - | - | - | - | - | - | 60 | 7 min | Alum | 0 | 0.5 | 5 | GAC | Anthracite
2022-07-18 07:17:00 AM | 65 | DAF | 5.92 | 5.95 | 0.33800000000000002 | 0.40500000000000003 | 86.9 | 10 | - | 0.03 | 0.35299999999999998 | - | - | - | 60 | 7 min | Alum | 0 | 0.5 | 5 | GAC | Anthracite
2022-07-18 07:19:00 AM | 65 | F1 | - | 5.94 | 5.8999999999999997E-2 | 9.8000000000000004E-2 | 93.7 | 2 | - | 0.03 | 2.9000000000000001E-2 | - | 13.2 | 13.04 | 60 | 7 min | Alum | 0 | 0.5 | 5 | GAC | Anthracite
2022-07-18 07:20:00 AM | 65 | F2 | - | 5.92 | 8.3000000000000004E-2 | 9.8000000000000004E-2 | 92.9 | 2 | - | 0.02 | 2.1000000000000001E-2 | - | 13.6 | 3.96 | 60 | 7 min | Alum | 0 | 0.5 | 5 | GAC | Anthracite
2022-07-18 10:08:00 AM | 66 | Raw | - | 5.58 | 0.39 | 0.503 | 73.3 | 29 | - | - | - | - | - | - | 60 | 7 min | Alum | 0 | 0.5 | 5 | GAC | Anthracite
2022-07-18 10:09:00 AM | 66 | Rapid Mix | - | 6.15 | - | - | - | - | - | - | - | - | - | - | 60 | 7 min | Alum | 0 | 0.5 | 5 | GAC | Anthracite
2022-07-18 10:09:00 AM | 66 | DAF | 6.05 | 6.16 | 0.30099999999999999 | 0.39500000000000002 | 86.1 | 8 | - | - | - | - | - | - | 60 | 7 min | Alum | 0 | 0.5 | 5 | GAC | Anthracite
2022-07-18 10:10:00 AM | 66 | F1 | - | 6.11 | 6.7000000000000004E-2 | 0.112 | 93.5 | 0 | - | - | - | - | 16.5 | 12.85 | 60 | 7 min | Alum | 0 | 0.5 | 5 | GAC | Anthracite
2022-07-18 10:11:00 AM | 66 | F2 | - | 6.12 | 9.4E-2 | 0.109 | 92.6 | 0 | - | - | - | - | 16.899999999999999 | 4.01 | 60 | 7 min | Alum | 0 | 0.5 | 5 | GAC | Anthracite
2022-07-19 07:31:00 AM | 67 | Raw | - | 5.58 | 0.379 | 0.45400000000000001 | 73.7 | 28 | 2.7E-2 | - | 4.5999999999999999E-2 | - | - | - | 80 | 7 min | Alum | 0 | 0.5 | 5 | GAC | Anthracite
2022-07-19 07:31:00 AM | 67 | Rapid Mix | - | 6.17 | - | 1.53 | - | - | - | - | - | - | - | - | 80 | 7 min | Alum | 0 | 0.5 | 5 | GAC | Anthracite
2022-07-19 07:32:00 AM | 67 | DAF | 6.11 | 6.14 | 0.29799999999999999 | 0.374 | 89.1 | 6 | 0.02 | - | 0.29299999999999998 | - | - | - | 80 | 7 min | Alum | 0 | 0.5 | 5 | GAC | Anthracite
2022-07-19 07:33:00 AM | 67 | F1 | - | 6.11 | 4.5999999999999999E-2 | 9.5000000000000001E-2 | 94.7 | 0 | 2.1000000000000001E-2 | - | 2.1999999999999999E-2 | - | 19.100000000000001 | 14.02 | 80 | 7 min | Alum | 0 | 0.5 | 5 | GAC | Anthracite
2022-07-19 07:33:00 AM | 67 | F2 | - | 6.09 | 3.2000000000000001E-2 | 8.8999999999999996E-2 | 93.7 | 0 | 0.02 | - | 0.01 | - | 19.600000000000001 | 5.29 | 80 | 7 min | Alum | 0 | 0.5 | 5 | GAC | Anthracite
2022-07-19 10:41:59 AM | 68 | Raw | - | 5.58 | 0.38300000000000001 | 0.47099999999999997 | 73.7 | 28 | - | - | - | - | - | - | 80 | 7 min | Alum | 0 | 0.5 | 5 | GAC | Anthracite
2022-07-19 10:41:59 AM | 68 | Rapid Mix | - | 6.16 | - | - | - | - | - | - | - | - | - | - | 80 | 7 min | Alum | 0 | 0.5 | 5 | GAC | Anthracite
2022-07-19 10:43:00 AM | 68 | DAF | 6.08 | 6.1 | 0.29099999999999998 | 0.36099999999999999 | 88.4 | 9 | - | - | - | - | - | - | 80 | 7 min | Alum | 0 | 0.5 | 5 | GAC | Anthracite
2022-07-19 10:43:59 AM | 68 | F1 | - | 6.11 | 4.4999999999999998E-2 | 0.10299999999999999 | 94.1 | 1 | - | - | - | - | 22.3 | 14.17 | 80 | 7 min | Alum | 0 | 0.5 | 5 | GAC | Anthracite
2022-07-19 10:45:00 AM | 68 | F2 | - | 6.14 | 3.4000000000000002E-2 | 9.4E-2 | 92.8 | 1 | - | - | - | - | 22.7 | 5.43 | 80 | 7 min | Alum | 0 | 0.5 | 5 | GAC | Anthracite
2022-07-20 11:26:59 AM | 69 | Raw | - |  | 0.379 | 0.46899999999999997 | 73.5 | 26 | - | - | 4.7E-2 | - | - | - | 90 | 7 min | Alum | 0 | 0.5 | 5 | GAC | Anthracite | 3.5230000000000001
2022-07-20 11:26:59 AM | 69 | Rapid Mix | - | 6.49 | - | 1.48 | - | - | - | - | - | - | - | - | 90 | 7 min | Alum | 0 | 0.5 | 5 | GAC | Anthracite
2022-07-20 11:28:00 AM | 69 | DAF | 6.81 | 6.45 | 0.22600000000000001 | 0.312 | 88.7 | 9 | - | - | 0.35599999999999998 | - | - | - | 90 | 7 min | Alum | 0 | 0.5 | 5 | GAC | Anthracite | 2.3340000000000001
2022-07-20 11:28:59 AM | 69 | F1 | - | 6.35 | 6.0999999999999999E-2 | 0.104 | 92.8 | 3 | - | - | 0.06 | - | 24.8 | 13.85 | 90 | 7 min | Alum | 0 | 0.5 | 5 | GAC | Anthracite | 1.7649999999999999
2022-07-20 11:30:00 AM | 69 | F2 | - | 6.34 | 5.7000000000000002E-2 | 0.121 | 91.4 | 4 | - | - | 0.10100000000000001 | - | 25.2 | 5.27 | 90 | 7 min | Alum | 0 | 0.5 | 5 | GAC | Anthracite | 1.9990000000000001
2022-07-21 07:24:00 AM | 70 | Raw | - | 5.61 | 0.38200000000000001 | 0.46800000000000003 | 74.900000000000006 | 28 | - | - | - | - | - | - | 90 | 7 min | Alum | 0 | 0.5 | 5 | GAC | Anthracite
2022-07-21 07:24:00 AM | 70 | Rapid Mix | - | 6.01 | - | - | - | - | - | - | - | - | - | - | 90 | 7 min | Alum | 0 | 0.5 | 5 | GAC | Anthracite
2022-07-21 07:25:00 AM | 70 | DAF | 5.92 | 5.94 | 0.26100000000000001 | 0.35299999999999998 | 89.3 | 8 | - | - | 0.376 | - | - | - | 90 | 7 min | Alum | 0 | 0.5 | 5 | GAC | Anthracite
2022-07-21 07:26:00 AM | 70 | F1 | - | 5.91 | 7.4999999999999997E-2 | 0.113 | 94 | 2 | - | - | 8.5000000000000006E-2 | - | 27.4 | 14.55 | 90 | 7 min | Alum | 0 | 0.5 | 5 | GAC | Anthracite
2022-07-21 07:26:00 AM | 70 | F2 | - | 5.89 | 7.1999999999999995E-2 | 0.14099999999999999 | 92.7 | 3 | - | - | 9.5000000000000001E-2 | - | 27.8 | 6.26 | 90 | 7 min | Alum | 0 | 0.5 | 5 | GAC | Anthracite
2022-07-21 11:11:00 AM | 71 | Raw | - | 5.62 | 0.39600000000000002 | 0.46400000000000002 | 73.8 |  | - | - | - | - | - | - | 90 | 7 min | Alum | 0 | 0.5 | 5 | GAC | Anthracite
2022-07-21 11:12:00 AM | 71 | Rapid Mix | - | 6.16 | - | - | - | - | - | - | - | - | - | - | 90 | 7 min | Alum | 0 | 0.5 | 5 | GAC | Anthracite
2022-07-21 11:12:00 AM | 71 | DAF | 6.11 | 6.16 | 0.23599999999999999 | 0.33500000000000002 | 89.3 | 7 | - | - | - | - | - | - | 90 | 7 min | Alum | 0 | 0.5 | 5 | GAC | Anthracite
2022-07-21 11:13:00 AM | 71 | F1 | - | 6.98 | 0.122 | 0.17899999999999999 | 92.6 | 3 | - | - | - | - | 31.7 | 14.64 | 90 | 7 min | Alum | 0 | 0.5 | 5 | GAC | Anthracite
2022-07-21 11:13:00 AM | 71 | F2 | - | 6.07 | 0.11700000000000001 | 0.16400000000000001 | 91.8 | 4 | - | - | - | - | 32.1 | 6.36 | 90 | 7 min | Alum | 0 | 0.5 | 5 | GAC | Anthracite
2022-07-22 09:02:00 AM | 72 | Raw | - | 5.59 | 0.38200000000000001 | 0.45700000000000002 | 73.900000000000006 | 27 | - | - | - | - | - | - | 30 | 23 min | Alum | 0 | 0.5 | 5 | GAC | Anthracite |  |  | Sampled for BV Labs
2022-07-22 09:02:00 AM | 72 | Rapid Mix | - | 5.97 | - | - | - | - | - | - | - | - | - | - | 30 | 23 min | Alum | 0 | 0.5 | 5 | GAC | Anthracite
2022-07-22 09:03:00 AM | 72 | DAF | 5.84 | 5.99 | 0.28899999999999998 | 0.36099999999999999 | 86.9 | 10 | - | - | - | - | - | - | 30 | 23 min | Alum | 0 | 0.5 | 5 | GAC | Anthracite |  |  | Sampled for BV Labls
2022-07-22 09:03:59 AM | 72 | F1 | - | 6.01 | 5.6000000000000001E-2 | 0.113 | 93.8 | 3 | - | - | - | - | 33.200000000000003 | 15 | 30 | 23 min | Alum | 0 | 0.5 | 5 | GAC | Anthracite |  |  | Sampled for BV Labs
2022-07-22 09:05:00 AM | 72 | F2 | - | 5.98 | 5.6000000000000001E-2 | 0.128 | 92.9 | 4 | - | - | - | - | 33.6 | 7.23 | 30 | 23 min | Alum | 0 | 0.5 | 5 | GAC | Anthracite |  |  | Sampled for BV Labs
2022-07-25 07:08:00 AM | 73 | Raw | - | 5.59 | 0.34899999999999998 | 0.49099999999999999 | 73.8 | 26 | - | - | 4.3999999999999997E-2 | - | - | - | 40 | 23 min | Alum | 0 | 0.5 | 5 | GAC | Anthracite |  |  | Dal Turbidity = 0.523 NTU
2022-07-25 07:08:00 AM | 73 | Rapid Mix | - |  | - | - | - | - | - | - | - | - | - | - | 40 | 23 min | Alum | 0 | 0.5 | 5 | GAC | Anthracite
2022-07-25 07:09:00 AM | 73 | DAF | 6.01 | 6.31 | 0.222 | 0.30299999999999999 | 88.1 | 6 | - | - | 0.24099999999999999 | - | - | - | 40 | 23 min | Alum | 0 | 0.5 | 5 | GAC | Anthracite |  |  | Dal Turbidity = 0.236 NTU
2022-07-25 07:09:59 AM | 73 | F1 | - | 6.11 | 8.4000000000000005E-2 | 0.122 | 91.3 | 1 | - | - | 3.1E-2 | - | 35.9 | 15 | 40 | 23 min | Alum | 0 | 0.5 | 5 | GAC | Anthracite |  |  | Dal Turbidity = 0.115 NTU
2022-07-25 07:09:59 AM | 73 | F2 | - | 6.12 | 7.8E-2 | 0.14599999999999999 | 90.3 | 1 | - | - | 4.9000000000000002E-2 | - | 36.299999999999997 | 7.86 | 40 | 23 min | Alum | 0 | 0.5 | 5 | GAC | Anthracite |  |  | Dal Turbidity = 0.143 NTU
2022-07-26 08:14:59 AM | 74 | Raw | - | 5.71 | 0.38800000000000001 | 0.47299999999999998 | 74.5 | 25 | - | 0.08 | 4.3999999999999997E-2 | - | - | - | 40 | 23 min | Alum | 0.15 | 0.5 | 5 | GAC | Anthracite
2022-07-26 08:14:59 AM | 74 | Rapid Mix | - | 6.18 | - | 1.45 | - | - | - | - | - | - | - | - | 40 | 23 min | Alum | 0.15 | 0.5 | 5 | GAC | Anthracite
2022-07-26 08:14:59 AM | 74 | DAF | 5.89 | 6.22 | 0.20599999999999999 | 0.27900000000000003 | 89 | 6 | - | 0.03 | 0.20599999999999999 | - | - | - | 40 | 23 min | Alum | 0.15 | 0.5 | 5 | GAC | Anthracite
2022-07-26 08:16:00 AM | 74 | F1 | - | 6.12 | 0.112 | 0.11600000000000001 | 92.9 | 2 | - | 0.01 | 2.8000000000000001E-2 | - | 1.1000000000000001 | 11.62 | 40 | 23 min | Alum | 0.15 | 0.5 | 5 | GAC | Anthracite
2022-07-26 08:16:00 AM | 74 | F2 | - | 6.09 | 7.0000000000000007E-2 | 0.121 | 91.4 | 2 | - | 0.01 | 2.1999999999999999E-2 | - | 1.5 | 2.64 | 40 | 23 min | Alum | 0.15 | 0.5 | 5 | GAC | Anthracite
2022-07-26 10:58:00 AM | 75 | Raw | - | 5.58 | 0.316 | 0.48899999999999999 | 74.3 | 24 | 2.5999999999999999E-2 | 0.08 | 4.5999999999999999E-2 | - | - | - | 40 | 23 min | Alum | 0.15 | 0.5 | 5 | GAC | Anthracite | 3.9550000000000001 |  | ICP MS samples @ Dal
2022-07-26 NA | 75 | Rapid Mix | - | 6.2 | - | - | - | - | - | - | - | - | - | - | 40 | 23 min | Alum | 0.15 | 0.5 | 5 | GAC | Anthracite
2022-07-26 10:59:00 AM | 75 | DAF | 5.76 | 6.19 | 0.186 | 0.253 | 89.1 | 6 | 0.02 | 0.03 | 0.19500000000000001 | - | - | - | 40 | 23 min | Alum | 0.15 | 0.5 | 5 | GAC | Anthracite | 2.2730000000000001 |  | ICP MS samples @ Dal
2022-07-26 11:00:00 AM | 75 | F1 | - | 6.14 | 9.0999999999999998E-2 | 0.105 | 92.7 | 1 | 1.4999999999999999E-2 | 0.01 | 2.1000000000000001E-2 | - | 4.2 | 11.53 | 40 | 23 min | Alum | 0.15 | 0.5 | 5 | GAC | Anthracite | 1.8720000000000001 |  | ICP MS samples @ Dal
2022-07-26 11:01:00 AM | 75 | F2 | - | 6.15 | 6.3E-2 | 0.114 | 91.2 | 2 | 1.6E-2 | 0.01 | 1.6E-2 | - | 4.5999999999999996 | 2.72 | 40 | 23 min | Alum | 0.15 | 0.5 | 5 | GAC | Anthracite | 2.0350000000000001 |  | ICP MS samples @ Dal
2022-07-27 08:56:00 AM | 76 | Raw | - | 5.86 | 0.308 | 0.47299999999999998 | 74.900000000000006 | 26 | - | 0.08 | 4.5999999999999999E-2 | - | - | - | 40 | 23 min | Alum | 0.15 | 0.5 | 5 | GAC | Anthracite |  |  | Dal Turbidity = 0.429 NTU
2022-07-27 08:56:00 AM | 76 | Rapid Mix | - | 6.23 | - | 1.49 | - | - | - | - | - | - | - | - | 40 | 23 min | Alum | 0.15 | 0.5 | 5 | GAC | Anthracite
2022-07-27 08:57:00 AM | 76 | DAF | 5.82 | 6.24 | 0.216 | 0.26900000000000002 | 88.8 | 7 | - | 0.03 | 0.222 | - | - | - | 40 | 23 min | Alum | 0.15 | 0.5 | 5 | GAC | Anthracite |  |  | Dal Turbidity = 0.219 NTU
2022-07-27 08:58:00 AM | 76 | F1 | - | 6.22 | 8.6999999999999994E-2 | 0.115 | 93.3 | 2 | - | 0.01 | 1.7999999999999999E-2 | - | 5.8 | 11.91 | 40 | 23 min | Alum | 0.15 | 0.5 | 5 | GAC | Anthracite |  |  | Dal Turbidity = 0.133 NTU
2022-07-27 08:58:00 AM | 76 | F2 | - | 6.23 | 5.5E-2 | 0.10100000000000001 | 91.9 | 2 | - | 0.01 | 1.7999999999999999E-2 | - | 6.2 | 3.02 | 40 | 23 min | Alum | 0.15 | 0.5 | 5 | GAC | Anthracite |  |  | Dal Turbidity = 0.106 NTU
2022-07-27 11:33:00 AM | 77 | Raw | - | 5.91 | 0.92 | 0.46700000000000003 |  | 25 | 2.7E-2 | - | 4.1000000000000002E-2 | - | - | - | 40 | 23 min | Alum | 0.15 | 0.5 | 5 | GAC | Anthracite |  |  | ICP MS samples @ Dal
2022-07-27 11:33:00 AM | 77 | Rapid Mix | - | 6.23 | - | - | - | - | - | - | - | - | - | - | 40 | 23 min | Alum | 0.15 | 0.5 | 5 | GAC | Anthracite
2022-07-27 11:34:00 AM | 77 | DAF | 5.82 | 6.22 | 0.191 | 0.251 | 90 | 6 | 2.3E-2 | - | 0.21299999999999999 | - | - | - | 40 | 23 min | Alum | 0.15 | 0.5 | 5 | GAC | Anthracite |  |  | ICP MS samples @ Dal
2022-07-27 11:35:00 AM | 77 | F1 | - | 6.18 | 0.105 | 0.104 | 92.9 | 2 | 1.9E-2 | - | 1.7999999999999999E-2 | - | 8.5 | 11.75 | 40 | 23 min | Alum | 0.15 | 0.5 | 5 | GAC | Anthracite |  |  | ICP MS samples @ Dal
2022-07-27 11:35:00 AM | 77 | F2 | - | 6.15 | 0.05 | 0.122 | 92.1 | 2 | 1.7999999999999999E-2 | - | 1.9E-2 | - | 8.9 | 2.91 | 40 | 23 min | Alum | 0.15 | 0.5 | 5 | GAC | Anthracite |  |  | ICP MS samples @ Dal
2022-07-28 09:38:00 AM | 78 | Raw | - | 5.76 | 0.28499999999999998 | 0.47299999999999998 | 74.2 | 24 | - | 7.0000000000000007E-2 | 4.4999999999999998E-2 | - | - | - | 40 | 23 min | Alum | 0.15 | 0.5 | 5 | GAC | Anthracite
2022-07-28 09:38:00 AM | 78 | Rapid Mix | - | 6.19 | - | - | - | - | - | - | - | - | - | - | 40 | 23 min | Alum | 0.15 | 0.5 | 5 | GAC | Anthracite
2022-07-28 09:39:00 AM | 78 | DAF | 6.57 | 6.22 | 0.19500000000000001 | 0.25700000000000001 | 88.8 | 7 | 2.4E-2 | 0.03 | 0.17299999999999999 | - | - | - | 40 | 23 min | Alum | 0.15 | 0.5 | 5 | GAC | Anthracite
2022-07-28 09:40:00 AM | 78 | F1 | - | 6.18 | 0.12 | 0.112 | 92.4 | 2 | 2.5000000000000001E-2 | 0.01 | 2.9000000000000001E-2 | - | 11.1 | 11.81 | 40 | 23 min | Alum | 0.15 | 0.5 | 5 | GAC | Anthracite
2022-07-28 09:41:00 AM | 78 | F2 | - | 6.2 | 5.3999999999999999E-2 | 0.104 | 91.6 | 3 | 1.9E-2 | 0.01 | 1.7999999999999999E-2 | - | 11.5 | 2.92 | 40 | 23 min | Alum | 0.15 | 0.5 | 5 | GAC | Anthracite
2022-07-29 09:07:59 AM | 79 | Raw | - | 5.57 | 0.26800000000000002 | 0.41699999999999998 | 75.099999999999994 | 24 | 2.7E-2 | 0.02 | 4.2000000000000003E-2 | - | - | - | 40 | 23 min | Alum | 0.15 | 0.5 | 5 | GAC | Anthracite |  |  | ICP MS samples @ Dal
2022-07-29 09:09:00 AM | 79 | Rapid Mix | - | 6.02 | - | 1.87 | - | - | - | - | - | - | - | - | 40 | 23 min | Alum | 0.15 | 0.5 | 5 | GAC | Anthracite
2022-07-29 09:07:59 AM | 79 | DAF | 6.36 | 6.04 | 0.186 | 0.247 | 90.4 | 6 | 2.7E-2 | 0.01 | 0.184 | - | - | - | 40 | 23 min | Alum | 0.15 | 0.5 | 5 | GAC | Anthracite |  |  | ICP MS samples @ Dal
2022-07-29 09:10:00 AM | 79 | F1 | - | 6.05 | 8.7999999999999995E-2 | 0.10100000000000001 | 93.9 | 2 | 2.4E-2 | 0 | 1.2999999999999999E-2 | - | 15 | 13.07 | 40 | 23 min | Alum | 0.15 | 0.5 | 5 | GAC | Anthracite |  |  | ICP MS samples @ Dal
2022-07-29 09:11:00 AM | 79 | F2 | - | 6.06 | 4.9000000000000002E-2 | 9.8000000000000004E-2 | 92.8 | 4 | 0.02 | 0 | 8.0000000000000002E-3 | - | 15.4 | 3.66 | 40 | 23 min | Alum | 0.15 | 0.5 | 5 | GAC | Anthracite |  |  | ICP MS samples @ Dal
2022-08-02 07:07:00 AM | 80 | Raw | - | 5.78 | 0.20599999999999999 | 0.41899999999999998 | - | - | - | 0.02 | 4.4999999999999998E-2 | - | - | - | 40 | 23 min | Alum | 0.15 | 0.5 | 5 | GAC | Anthracite
2022-08-02 07:08:00 AM | 80 | Rapid Mix | - | 6.72 | - | 1.34 | - | - | - | - | - | - | - | - | 40 | 23 min | Alum | 0.15 | 0.5 | 5 | GAC | Anthracite
2022-08-02 07:07:00 AM | 80 | DAF | 6.41 | 6.69 | 0.29599999999999999 | 0.35499999999999998 | - | - | - | 0 | 0.29499999999999998 | - | - | - | 40 | 23 min | Alum | 0.15 | 0.5 | 5 | GAC | Anthracite
2022-08-02 07:09:59 AM | 80 | F1 | - | 6.65 | 0.115 | 0.124 | - | - | - | 0 | 2.1000000000000001E-2 | - | 18 | 13.16 | 40 | 23 min | Alum | 0.15 | 0.5 | 5 | GAC | Anthracite
2022-08-02 07:11:00 AM | 80 | F2 | - | 6.68 | 6.3E-2 | 0.11700000000000001 | - | - | - | 0 | 2.5000000000000001E-2 | - | 18.399999999999999 | 3.66 | 40 | 23 min | Alum | 0.15 | 0.5 | 5 | GAC | Anthracite
2022-08-02 10:05:00 AM | 81 | Raw | - | 5.79 | 0.20100000000000001 | 0.41599999999999998 | - | - | 2.8000000000000001E-2 | 0.02 | 4.7E-2 | - | - | - | 40 | 23 min | Alum | 0.15 | 0.5 | 5 | GAC | Anthracite | 3.286 |  | DBPfp @CWRS; ICP MS samples @CWRS
2022-08-02 10:06:00 AM | 81 | Rapid Mix | - | 6.45 | - | 1.43 | - | - | - | - | - | - | - | - | 40 | 23 min | Alum | 0.15 | 0.5 | 5 | GAC | Anthracite
2022-08-02 10:06:00 AM | 81 | DAF | 6.22 | 6.48 | 0.19600000000000001 | 0.26100000000000001 | - | - | 2.4E-2 | 0 | - | - | - | - | 40 | 23 min | Alum | 0.15 | 0.5 | 5 | GAC | Anthracite | 2.2149999999999999 |  | DBPfp @CWRS; ICP MS samples @CWRS
2022-08-02 10:07:00 AM | 81 | F1 | - | 6.43 | 8.6999999999999994E-2 | 0.11899999999999999 | - | - | 1.9E-2 | 0 | 2.5999999999999999E-2 | - | 21 | 13.12 | 40 | 23 min | Alum | 0.15 | 0.5 | 5 | GAC | Anthracite | 1.839 |  | DBPfp @CWRS; ICP MS samples @CWRS
2022-08-02 10:08:00 AM | 81 | F2 | - | 6.41 | 5.7000000000000002E-2 | 0.111 | - | - | 1.7000000000000001E-2 | 0 | 0.03 | - | 21.4 | 3.81 | 40 | 23 min | Alum | 0.15 | 0.5 | 5 | GAC | Anthracite | 2.0169999999999999 |  | DBPfp @CWRS; ICP MS samples @CWRS
2022-08-03 09:23:00 AM | 82 | Raw | - | 5.65 | 0.17899999999999999 | 0.441 | 75.099999999999994 | 22 | 3.5000000000000003E-2 | 0.02 | 4.2999999999999997E-2 | - | - | - | 40 | 23 min | Alum | 0.15 | 0.5 | 5 | GAC | Anthracite |  |  | ICP MS samples @ CWRS
2022-08-03 09:23:00 AM | 82 | Rapid Mix | - | 6.32 | - | 1.38 | - | - | - | - | - | - | - | - | 40 | 23 min | Alum | 0.15 | 0.5 | 5 | GAC | Anthracite
2022-08-03 09:24:00 AM | 82 | DAF | 6.22 | 6.32 | 0.20100000000000001 | 0.27700000000000002 | 88.8 | 6 | 3.1E-2 | 0.01 | 0.21099999999999999 | - | - | - | 40 | 23 min | Alum | 0.15 | 0.5 | 5 | GAC | Anthracite |  |  | ICP MS samples @ CWRS
2022-08-03 09:25:00 AM | 82 | F1 | - | 6.29 | 7.6999999999999999E-2 | 0.121 | 92.1 | 2 | 2.4E-2 | 0 | 1.6E-2 | - | 25.8 | 13.45 | 40 | 23 min | Alum | 0.15 | 0.5 | 5 | GAC | Anthracite |  |  | ICP MS samples @ CWRS
2022-08-03 09:26:00 AM | 82 | F2 | - | 6.31 | 4.1000000000000002E-2 | 0.129 | 91.1 | 2 | 2.3E-2 | 0 | 1.6E-2 | - | 26.2 | 4.21 | 40 | 23 min | Alum | 0.15 | 0.5 | 5 | GAC | Anthracite |  |  | ICP MS samples @ CWRS
2022-08-04 10:20:00 AM | 83 | Raw | - | 5.63 | 0.16900000000000001 | 0.41799999999999998 | 75.8 | 21 | 2.8000000000000001E-2 | 0.02 | 3.5999999999999997E-2 | - | - | - | 40 | 23 min | Alum | 0.15 | 0.5 | 5 | GAC | Anthracite
2022-08-04 10:21:00 AM | 83 | Rapid Mix | - | - | - | - | - | - | - | - | - | - | - | - | 40 | 23 min | Alum | 0.15 | 0.5 | 5 | GAC | Anthracite
2022-08-04 10:21:00 AM | 83 | DAF | 5.98 | 6.05 | 0.17899999999999999 | 0.23499999999999999 | 89.4 | 5 | 2.5999999999999999E-2 | 0 | 0.152 | - | - | - | 40 | 23 min | Alum | 0.15 | 0.5 | 5 | GAC | Anthracite
2022-08-04 10:22:00 AM | 83 | F1 | - | 6.03 | 4.2999999999999997E-2 | 0.107 | 93.1 | 2 | 2.5000000000000001E-2 | 0 | 1.4999999999999999E-2 | - | 33.5 | 13.6 | 40 | 23 min | Alum | 0.15 | 0.5 | 5 | GAC | Anthracite
2022-08-04 10:23:00 AM | 83 | F2 | - | 6.06 | 7.9000000000000001E-2 | 0.129 | 92 | 2 | 2.4E-2 | 0 | 1.4E-2 | - | 33.9 | 4.3899999999999997 | 40 | 23 min | Alum | 0.15 | 0.5 | 5 | GAC | Anthracite
2022-08-05 09:48:00 AM | 84 | Raw | - | 5.62 | 0.156 | 0.41199999999999998 | 75.900000000000006 | 22 | - | 0.02 | 4.9000000000000002E-2 | - | - | - | 40 | 23 min | Alum | 0 | 0.5 | 5 | GAC | Anthracite
2022-08-05 09:48:00 AM | 84 | Rapid Mix | - | 6.14 | - | 1.42 | - | - | - | - | - | - | - | - | 40 | 23 min | Alum | 0 | 0.5 | 5 | GAC | Anthracite
2022-08-05 09:48:59 AM | 84 | DAF | 6.02 | 6.12 | 0.17899999999999999 | 0.25800000000000001 | 89.8 | 6 | - | 0 | 0.186 | - | - | - | 40 | 23 min | Alum | 0 | 0.5 | 5 | GAC | Anthracite
2022-08-05 09:48:59 AM | 84 | F2 | - | 6.13 | 7.4999999999999997E-2 | 0.11799999999999999 | 92.1 | 2 | - | 0 | 1.2E-2 | - | 56.3 | 5.48 | 40 | 23 min | Alum | 0 | 0.5 | 5 | GAC | Anthracite
2022-08-08 08:12:00 AM | 85 | Raw | - | 5.72 | - | 0.42099999999999999 | 76.099999999999994 | 22 | - | 0.02 | 4.4999999999999998E-2 | - | - | - | 40 | 23 min | Alum | 0 | 0.5 | 5 | GAC | Anthracite
2022-08-08 08:13:00 AM | 85 | Rapid Mix | - | 6.35 | - | 1.31 | - | - | - | - | - | - | - | - | 40 | 23 min | Alum | 0 | 0.5 | 5 | GAC | Anthracite
2022-08-08 08:12:00 AM | 85 | DAF | 5.97 | 6.33 | 0.19800000000000001 | 0.25700000000000001 | 90.1 | 6 | - | 0 | 0.17299999999999999 | - | - | - | 40 | 23 min | Alum | 0 | 0.5 | 5 | GAC | Anthracite
2022-08-08 08:13:00 AM | 85 | F2 | - | 6.29 | 8.1000000000000003E-2 | 0.123 | 91.8 | 2 | - | 0 | 1.7000000000000001E-2 | - | 59 | 5.54 | 40 | 23 min | Alum | 0 | 0.5 | 5 | GAC | Anthracite
2022-08-09 06:54:00 AM | 86 | Raw | - | 5.62 | - | 0.42599999999999999 | 75.900000000000006 | 21 | - | 0.02 | 4.5999999999999999E-2 | - | - | - | 40 | 23 min | Alum | 0 | 0.5 | 5 | GAC | Anthracite
2022-08-09 06:56:00 AM | 86 | Rapid Mix | - | 5.96 | - | - | - | - | - | - | - | - | - | - | 40 | 23 min | Alum | 0 | 0.5 | 5 | GAC | Anthracite
2022-08-09 06:55:00 AM | 86 | DAF | 5.84 | 6.02 | 0.185 | 0.24099999999999999 | 90 | 6 | - | 0 | 0.17799999999999999 | - | - | - | 40 | 23 min | Alum | 0 | 0.5 | 5 | GAC | Anthracite
2022-08-09 06:56:00 AM | 86 | F2 | - | 6.03 | 6.9000000000000006E-2 | 0.126 | 92.4 | 2 | - | 0 | 1.9E-2 | - | 63.2 | 6.32 | 40 | 23 min | Alum | 0 | 0.5 | 5 | GAC | Anthracite
2022-08-09 09:17:00 AM | 87 | Raw | - | 5.65 | - | 0.40600000000000003 | 76 | 21 | - | 0.02 | 4.4999999999999998E-2 | - | - | - | 40 | 23 min | Alum | 0 | 0.5 | 5 | GAC | Anthracite
2022-08-09 09:20:00 AM | 87 | Rapid Mix | - | 6.03 | - | - | - | - | - | - | - | - | - | - | 40 | 23 min | Alum | 0 | 0.5 | 5 | GAC | Anthracite
2022-08-09 09:19:00 AM | 87 | DAF | 5.88 | 6.07 | 0.184 | 0.23200000000000001 | 90.3 | 5 | - | 0 | 0.16500000000000001 | - | - | - | 40 | 23 min | Alum | 0 | 0.5 | 5 | GAC | Anthracite
2022-08-09 09:21:00 AM | 87 | F2 | - | 6.04 | 7.4999999999999997E-2 | 0.115 | 92.9 | 1 | - | 0 | 1.4999999999999999E-2 | - | 65.900000000000006 | 6.48 | 40 | 23 min | Alum | 0 | 0.5 | 5 | GAC | Anthracite
2022-08-10 07:54:59 AM | 88 | Raw | - | 5.81 | 0.34499999999999997 | 0.40799999999999997 | 75.8 | 20 | - | 0.02 | 3.5999999999999997E-2 | - | - | - | 40 | 23 min | Alum | 0 | 0.5 | 5 | GAC | Anthracite
2022-08-10 07:56:59 AM | 88 | Rapid Mix | - | 6.27 | - | - | - | - | - | - | - | - | - | - | 40 | 23 min | Alum | 0 | 0.5 | 5 | GAC | Anthracite
2022-08-10 07:54:59 AM | 88 | DAF | 6.07 | 6.29 | 0.21199999999999999 | 0.25700000000000001 | 89.2 | 5 | - | 0 | 0.19700000000000001 | - | - | - | 40 | 23 min | Alum | 0 | 0.5 | 5 | GAC | Anthracite
2022-08-10 07:56:00 AM | 88 | F2 | - | 6.28 | 6.4000000000000001E-2 | 0.108 | 91.9 | 2 | - | 0 | 1.2E-2 | - | 69.599999999999994 | 6.46 | 40 | 23 min | Alum | 0 | 0.5 | 5 | GAC | Anthracite
2022-08-10 11:17:00 AM | 89 | Raw | - | 5.82 | 0.34699999999999998 | 0.40899999999999997 | 76.2 | 21 | - | 0.02 | 4.2000000000000003E-2 | - | - | - | 40 | 23 min | Alum | 0 | 0.5 | 5 | GAC | Anthracite
2022-08-10 11:18:00 AM | 89 | Rapid Mix | - | 6.27 | - | - | - | - | - | - | - | - | - | - | 40 | 23 min | Alum | 0 | 0.5 | 5 | GAC | Anthracite
2022-08-10 11:17:00 AM | 89 | DAF | 6.05 | 6.26 | 0.20100000000000001 | 0.25 | 89.2 | 5 | - | 0 | 0.21099999999999999 | - | - | - | 40 | 23 min | Alum | 0 | 0.5 | 5 | GAC | Anthracite
2022-08-10 11:18:59 AM | 89 | F2 | - | 6.25 | 6.8000000000000005E-2 | 0.104 | 91.6 | 2 | - | 0 | 1.9E-2 | - | 73.099999999999994 | 6.73 | 40 | 23 min | Alum | 0 | 0.5 | 5 | GAC | Anthracite
2022-08-11 09:10:00 AM | 90 | Raw | - | 5.84 | 0.35199999999999998 | 0.40400000000000003 | 76.5 | 20 | - | 0.02 | 3.4000000000000002E-2 | - | - | - | 40 | 7 min | Alum | 0 | 0.5 | 5 | GAC | Anthracite | 3.3380000000000001
2022-08-11 09:11:00 AM | 90 | Rapid Mix | - | 6.41 | - | 1.21 | - | - | - | - | - | - | - | - | 40 | 7 min | Alum | 0 | 0.5 | 5 | GAC | Anthracite
2022-08-11 09:10:00 AM | 90 | DAF | 6.04 | 6.38 | 0.35499999999999998 | 0.46100000000000002 | 85.8 | 10 | - | 0.01 | 0.29199999999999998 | - | - | - | 40 | 7 min | Alum | 0 | 0.5 | 5 | GAC | Anthracite | 2.4740000000000002
2022-08-11 09:11:59 AM | 90 | F1 | - | 6.28 | 6.0999999999999999E-2 | 0.127 | 92.9 | 1 | - | 0 | 2.1000000000000001E-2 | - | 1.1000000000000001 | 11.9 | 40 | 7 min | Alum | 0 | 0.5 | 5 | GAC | Anthracite | 1.944
2022-08-11 09:13:00 AM | 90 | F2 | - | 6.29 | 7.1999999999999995E-2 | 0.13100000000000001 | 91.6 | 2 | - | 0 | 1.9E-2 | - | 1.6 | 2.82 | 40 | 7 min | Alum | 0 | 0.5 | 5 | GAC | Anthracite | 2.1269999999999998
2022-08-12 08:26:59 AM | 91 | Raw | - | 5.79 | 0.34100000000000003 | 0.40300000000000002 | 76.3 | 21 | - | 0.02 | 4.5999999999999999E-2 | - | - | - | 40 | 7 min | Alum | 0 | 0.5 | 5 | GAC | Anthracite |  |  | Samples taken for BV Labs
2022-08-12 08:28:00 AM | 91 | Rapid Mix | - | 6.33 | - | 1.18 | - | - | - | - | - | - | - | - | 40 | 7 min | Alum | 0 | 0.5 | 5 | GAC | Anthracite
2022-08-12 08:26:59 AM | 91 | DAF | 6.04 | 6.31 | 0.379 | 0.42099999999999999 | 86.1 | 10 | - | 0 | 0.35399999999999998 | - | - | - | 40 | 7 min | Alum | 0 | 0.5 | 5 | GAC | Anthracite |  |  | Samples taken for BV Labs
2022-08-12 08:28:59 AM | 91 | F1 | - | 6.3 | 4.5999999999999999E-2 | 0.115 | 92.8 | 1 | - | 0 | 2.5999999999999999E-2 | - | 5.5 | 12.56 | 40 | 7 min | Alum | 0 | 0.5 | 5 | GAC | Anthracite |  |  | Samples taken for BV Labs
2022-08-12 08:28:59 AM | 91 | F2 | - | 6.31 | 4.7E-2 | 0.112 | 91.7 | 2 | - | 0 | 1.6E-2 | - | 6 | 3.32 | 40 | 7 min | Alum | 0 | 0.5 | 5 | GAC | Anthracite |  |  | Samples taken for BV Labs
2022-08-15 06:38:00 AM | 92 | Raw | - | 5.69 | 0.32100000000000001 | 0.39400000000000002 | 77.3 | 19 | - | 0.02 | 4.2999999999999997E-2 | - | - | - | 40 | 7 min | Alum | 0 | 0.5 | 5 | GAC | Anthracite
2022-08-15 06:39:00 AM | 92 | Rapid Mix | - | 6.07 | - | - | - | - | - | - | - | - | - | - | 40 | 7 min | Alum | 0 | 0.5 | 5 | GAC | Anthracite
2022-08-15 06:38:00 AM | 92 | DAF | 5.54 | 6.04 | 0.36399999999999999 | 0.439 | 87.7 | 10 | - | 0 | 0.34699999999999998 | - | - | - | 40 | 7 min | Alum | 0 | 0.5 | 5 | GAC | Anthracite
2022-08-15 06:40:00 AM | 92 | F1 | - | 6.03 | 4.3999999999999997E-2 | 0.114 | 93.9 | 1 | - | 0 | 1.2999999999999999E-2 | - | 8.4 | 12.85 | 40 | 7 min | Alum | 0 | 0.5 | 5 | GAC | Anthracite
2022-08-05 06:40:00 AM | 92 | F2 | - | 6.04 | 5.6000000000000001E-2 | 0.111 | 92.5 | 1 | - | 0 | 1.0999999999999999E-2 | - | 8.9 | 3.78 | 40 | 7 min | Alum | 0 | 0.5 | 5 | GAC | Anthracite
2022-08-15 10:19:00 AM | 93 | Raw | - | 5.71 | 0.315 | 0.38100000000000001 | 77.400000000000006 | 19 | - | 0.02 |  | - | - | - | 40 | 7 min | Alum | 0 | 0.5 | 5 | GAC | Anthracite | 3.411
2022-08-15 10:21:00 AM | 93 | Rapid Mix | - | 6.03 | - | 1.31 | - | - | - | - | - | - | - | - | 40 | 7 min | Alum | 0 | 0.5 | 5 | GAC | Anthracite
2022-08-15 10:19:00 AM | 93 | DAF | 5.62 | 6.06 | 0.36099999999999999 | 0.42199999999999999 | 87.1 | 9 | - | 0 | 0.307 | - | - | - | 40 | 7 min | Alum | 0 | 0.5 | 5 | GAC | Anthracite | 2.5089999999999999
2022-08-15 10:20:00 AM | 93 | F1 | - | 6.01 | 5.1999999999999998E-2 | 0.106 | 94 | 1 | - | 0 | 2.1999999999999999E-2 | - | 12.1 | 12.86 | 40 | 7 min | Alum | 0 | 0.5 | 5 | GAC | Anthracite | 2.202
2022-08-15 10:21:00 AM | 93 | F2 | - |  | 7.0999999999999994E-2 | 0.11700000000000001 | 92.7 | 2 | - | 0 | 1.2999999999999999E-2 | - | 12.6 | 3.83 | 40 | 7 min | Alum | 0 | 0.5 | 5 | GAC | Anthracite | 2.194
2022-08-16 07:03:00 AM | 94 | Raw | - | 5.79 | 0.315 | 0.38500000000000001 | 77 | 19 | - | 0.02 | 3.6999999999999998E-2 | - | - | - | 40 | 7 min | Alum | 0 | 0.5 | 5 | GAC | Anthracite
2022-08-16 07:04:00 AM | 94 | Rapid Mix | - | 6.34 | - | - | - | - | - | - | - | - | - | - | 40 | 7 min | Alum | 0 | 0.5 | 5 | GAC | Anthracite
2022-08-16 07:05:00 AM | 94 | DAF | 5.72 | 6.32 | 0.32600000000000001 | 0.41399999999999998 | 87.1 | 9 | - | 0 | 0.315 | - | - | - | 40 | 7 min | Alum | 0 | 0.5 | 5 | GAC | Anthracite
2022-08-16 07:05:00 AM | 94 | F2 | - | 6.28 | 6.9000000000000006E-2 | 0.124 | 92.6 | 2 | - | 0 | 3.5000000000000003E-2 | - | 33.799999999999997 | 6.87 | 40 | 7 min | Alum | 0 | 0.5 | 5 | GAC | Anthracite
2022-08-16 10:15:00 AM | 95 | Raw | - | 6.76 | 0.31900000000000001 | 0.379 | 76.8 | 19 | - | 0.02 | 4.1000000000000002E-2 | - | - | - | 40 | 7 min | Alum | 0 | 0.5 | 5 | GAC | Anthracite
2022-08-16 10:16:00 AM | 95 | Rapid Mix | - | 6.25 | - | - | - | - | - | - | - | - | - | - | 40 | 7 min | Alum | 0 | 0.5 | 5 | GAC | Anthracite
2022-08-16 10:15:00 AM | 95 | DAF | - | 6.18 | 0.308 | 0.42899999999999999 | 86.8 | 9 | - | 0 | 0.31900000000000001 | - | - | - | 40 | 7 min | Alum | 0 | 0.5 | 5 | GAC | Anthracite
2022-08-16 10:17:00 AM | 95 | F2 | - | 6.2 | 9.9000000000000005E-2 | 0.153 | 92.1 | 3 | - | 0 | 5.0999999999999997E-2 | - | 36.799999999999997 | 7.25 | 40 | 7 min | Alum | 0 | 0.5 | 5 | GAC | Anthracite
2022-08-17 09:52:59 AM | 96 | Raw | - | 5.78 | 0.317 | 0.38300000000000001 | 77.400000000000006 | 19 | - | 0.02 | 3.3000000000000002E-2 | - | - | - | 40 | 7 min | Alum | 0 | 0.5 | 5 | GAC | Anthracite | 3.3180000000000001
2022-08-17 09:54:00 AM | 96 | Rapid Mix | - | 6.25 | - | - | - | - | - | - | - | - | - | - | 40 | 7 min | Alum | 0 | 0.5 | 5 | GAC | Anthracite
2022-08-17 09:52:59 AM | 96 | DAF | 6.32 | 6.26 | 0.35199999999999998 | 0.434 | 86.5 | 9 | - | 0 | 0.36399999999999999 | - | - | - | 40 | 7 min | Alum | 0 | 0.5 | 5 | GAC | Anthracite | 2.4980000000000002
2022-08-17 09:55:00 AM | 96 | F2 | - | 6.27 | 0.113 | 0.16700000000000001 | 90.4 | 3 | - | 0 | 9.8000000000000004E-2 | - | 40.700000000000003 | 8.7100000000000009 | 40 | 7 min | Alum | 0 | 0.5 | 5 | GAC | Anthracite | 2.177
2022-08-18 08:09:00 AM | 97 | Raw | - | 5.65 | 0.30199999999999999 | 0.377 | 77.400000000000006 | 19 | - | 0.02 | 3.2000000000000001E-2 | - | - | - | 40 | 14 min | Alum | 0 | 0.5 | 5 | GAC | Anthracite
2022-08-18 08:11:00 AM | 97 | Rapid Mix | - | 6.29 | - | - | - | - | - | - | - | - | - | - | 40 | 14 min | Alum | 0 | 0.5 | 5 | GAC | Anthracite
2022-08-18 08:09:00 AM | 97 | DAF | 6.08 | 6.33 | 0.23899999999999999 | 0.32900000000000001 | 89.5 | 8 | - | 0 | 0.26200000000000001 | - | - | - | 40 | 14 min | Alum | 0 | 0.5 | 5 | GAC | Anthracite
2022-08-18 08:10:00 AM | 97 | F1 | - | 6.26 | 5.6000000000000001E-2 | 0.126 | 93.8 | 1 | - | 0 | 0.02 | - | 0.9 | 12.24 | 40 | 14 min | Alum | 0 | 0.5 | 5 | GAC | Anthracite
2022-08-18 08:10:00 AM | 97 | F2 | - | 6.27 | 7.0999999999999994E-2 | 0.11799999999999999 | 92.5 | 1 | - | 0 | 1.2999999999999999E-2 | - | 1.2 | 3.22 | 40 | 14 min | Alum | 0 | 0.5 | 5 | GAC | Anthracite
2022-08-18 10:22:00 AM | 98 | Raw | - | 5.72 | 0.29299999999999998 | 0.39500000000000002 | 77.599999999999994 | 19 | - | 0.02 | 3.5000000000000003E-2 | - | - | - | 40 | 14 min | Alum | 0 | 0.5 | 5 | GAC | Anthracite
2022-08-18 10:24:00 AM | 98 | Rapid Mix | - | 6.24 | - | - | - | - | - | - | - | - | - | - | 40 | 14 min | Alum | 0 | 0.5 | 5 | GAC | Anthracite
2022-08-18 10:22:00 AM | 98 | DAF | 6.01 | 6.23 | 0.248 | 0.33100000000000002 | 89.9 | 8 | - | 0 | 0.27700000000000002 | - | - | - | 40 | 14 min | Alum | 0 | 0.5 | 5 | GAC | Anthracite | 2.266
2022-08-18 10:23:00 AM | 98 | F1 | - | 6.25 | 4.8000000000000001E-2 | 0.128 | 93.8 | 1 | - | 0 | 1.7000000000000001E-2 | - | 3.8 | 12.2 | 40 | 14 min | Alum | 0 | 0.5 | 5 | GAC | Anthracite | 1.9079999999999999
2022-08-18 10:24:00 AM | 98 | F2 | - | 6.23 | 5.1999999999999998E-2 | 0.114 | 92.7 | 1 | - | 0 | 1.4999999999999999E-2 | - | 4.0999999999999996 | 3.08 | 40 | 14 min | Alum | 0 | 0.5 | 5 | GAC | Anthracite | 2.2559999999999998
2022-08-19 08:31:00 AM | 99 | Raw | - | 5.69 | 0.29299999999999998 | 0.36699999999999999 | 77.5 | 19 | - | 0.02 | 5.8999999999999997E-2 | - | - | - | 40 | 14 min | Alum | 0 | 0.5 | 5 | GAC | Anthracite
2022-08-19 08:33:00 AM | 99 | Rapid Mix | - | 6.18 | - | - | - | - | - | - | - | - | - | - | 40 | 14 min | Alum | 0 | 0.5 | 5 | GAC | Anthracite
2022-08-19 08:31:00 AM | 99 | DAF | 6.18 | 6.16 | 0.27600000000000002 | 0.33200000000000002 | 89.2 | 7 | - | 0 | 0.251 | - | - | - | 40 | 14 min | Alum | 0 | 0.5 | 5 | GAC | Anthracite
2022-08-19 08:32:00 AM | 99 | F1 | - | 6.13 | 6.3E-2 | 0.111 | 93.6 | 1 | - | 0 | 1.2E-2 | - | 6.3 | 12.45 | 40 | 14 min | Alum | 0 | 0.5 | 5 | GAC | Anthracite
2022-08-19 08:33:00 AM | 99 | F2 | - | 6.12 | 7.5999999999999998E-2 | 0.122 | 92.4 | 1 | - | 0 | 1.4E-2 | - | 6.6 | 3.35 | 40 | 14 min | Alum | 0 | 0.5 | 5 | GAC | Anthracite
2022-08-22 06:53:00 AM | 100 | Raw | - | 5.73 | 0.28499999999999998 | 0.40100000000000002 | 77.5 | 18 | - | 0.02 | 2.8000000000000001E-2 | - | - | - | 40 | 14 min | Alum | 0 | 0.5 | 5 | GAC | Anthracite
2022-08-22 06:55:00 AM | 100 | Rapid Mix | - | 6.3 | - | - | - | - | - | - | - | - | - | - | 40 | 14 min | Alum | 0 | 0.5 | 5 | GAC | Anthracite
2022-08-22 06:53:00 AM | 100 | DAF | 5.92 | 6.25 | 0.21199999999999999 | 0.34399999999999997 | 88.9 | 6 | - | 0 | 0.254 | - | - | - | 40 | 14 min | Alum | 0 | 0.5 | 5 | GAC | Anthracite
2022-08-22 06:54:00 AM | 100 | F1 | - | 6.27 | 5.7000000000000002E-2 | 0.14099999999999999 | 93.8 | 1 | - | 0 | 1.0999999999999999E-2 | - | 8.1999999999999993 | 12.6 | 40 | 14 min | Alum | 0 | 0.5 | 5 | GAC | Anthracite
2022-08-22 06:55:00 AM | 100 | F2 | - | 6.25 | 5.8999999999999997E-2 | 0.13500000000000001 | 92.2 | 1 | - | 0 | 1.0999999999999999E-2 | - | 8.5 | 3.57 | 40 | 14 min | Alum | 0 | 0.5 | 5 | GAC | Anthracite
2022-08-22 09:22:00 AM | 101 | Raw | - | 5.71 | 0.28100000000000003 | 0.29699999999999999 | 77.900000000000006 | 19 | - | 0.02 | 3.1E-2 | - | - | - | 40 | 14 min | Alum | 0 | 0.5 | 5 | GAC | Anthracite
2022-08-22 09:23:00 AM | 101 | Rapid Mix | - | 6.34 | - | - | - | - | - | - | - | - | - | - | 40 | 14 min | Alum | 0 | 0.5 | 5 | GAC | Anthracite
2022-08-22 09:22:00 AM | 101 | DAF | 5.93 | 6.27 | 0.17899999999999999 | 0.314 | 89.7 | 6 | - | 0 | 0.24199999999999999 | - | - | - | 40 | 14 min | Alum | 0 | 0.5 | 5 | GAC | Anthracite
2022-08-22 09:24:00 AM | 101 | F1 | - | 6.23 | 5.8999999999999997E-2 | 0.111 | 93.9 | 1 | - | 0 | 0.01 | - | 11.2 | 12.37 | 40 | 14 min | Alum | 0 | 0.5 | 5 | GAC | Anthracite
2022-08-22 09:24:00 AM | 101 | F2 | - | 6.22 | 6.3E-2 | 0.121 | 91.9 | 1 | - | 0 | 8.0000000000000002E-3 | - | 11.5 | 3.42 | 40 | 14 min | Alum | 0 | 0.5 | 5 | GAC | Anthracite
2022-08-23 08:49:00 AM | 102 | Raw | - | 5.71 | 0.27900000000000003 | 0.35299999999999998 | 78.2 | 18 | - | 0.02 | 0.03 | - | - | - | 40 | 14 min | Alum | 0 | 0.5 | 5 | GAC | Anthracite
2022-08-23 08:51:00 AM | 102 | Rapid Mix | - | 6.55 | - | - | - | - | - | - | - | - | - | - | 40 | 14 min | Alum | 0 | 0.5 | 5 | GAC | Anthracite
2022-08-23 08:49:00 AM | 102 | DAF | 5.81 | 6.31 | 0.192 | 0.313 | 89.6 | 5 | - | 0 | 0.30299999999999999 | - | - | - | 40 | 14 min | Alum | 0 | 0.5 | 5 | GAC | Anthracite
2022-08-23 08:50:00 AM | 102 | F1 | - | 6.23 | 4.3999999999999997E-2 | 0.125 | 93.8 | 1 | - | 0 | 1.6E-2 | - | 14.9 | 13.31 | 40 | 14 min | Alum | 0 | 0.5 | 5 | GAC | Anthracite
2022-08-23 08:50:00 AM | 102 | F2 | - | 6.25 | 4.7E-2 | 0.114 | 93 | 1 | - | 0 | 1.4E-2 | - | 15.2 | 3.91 | 40 | 14 min | Alum | 0 | 0.5 | 5 | GAC | Anthracite
2022-08-24 06:22:00 AM | 103 | Raw | - | 5.63 | 0.27900000000000003 | 0.35299999999999998 | 78.599999999999994 | 17 | - | 0.02 | 2.9000000000000001E-2 | - | - | - | 40 | 14 min | Alum | 0 | 0.5 | 5 | GAC | Anthracite
2022-08-24 06:24:00 AM | 103 | Rapid Mix | - | - | - | - | - | - | - | - | - | - | - | - | 40 | 14 min | Alum | 0 | 0.5 | 5 | GAC | Anthracite
2022-08-24 06:22:00 AM | 103 | DAF | 5.95 | 6.06 | 0.19400000000000001 | 0.30099999999999999 | 89.7 | 5 | - | 0 | 0.24299999999999999 | - | - | - | 40 | 14 min | Alum | 0 | 0.5 | 5 | GAC | Anthracite
2022-08-24 06:23:00 AM | 103 | F1 | - | 6.09 | 4.3999999999999997E-2 | 0.107 | 93.9 | 1 | - | 0 | 1.2E-2 | - | 22 | 13.83 | 40 | 14 min | Alum | 0 | 0.5 | 5 | GAC | Anthracite
2022-08-24 06:26:00 AM | 103 | F2 | - | 6.08 | 6.2E-2 | 0.109 | 92.9 | 1 | - | 0 | 8.9999999999999993E-3 | - | 36 | 5.41 | 40 | 14 min | Alum | 0 | 0.5 | 5 | GAC | Anthracite
2022-08-25 06:47:00 AM | 104 | Raw | - | 5.74 | 0.26900000000000002 | 0.373 | 77.5 | 19 | - | 0.02 | 3.4000000000000002E-2 | - | - | - | 40 | 14 min | Alum | 0 | 0.5 | 5 | GAC | Anthracite
2022-08-25 06:49:00 AM | 104 | Rapid Mix | - | 6.33 | - | - | - | - | - | - | - | - | - | - | 40 | 14 min | Alum | 0 | 0.5 | 5 | GAC | Anthracite
2022-08-25 06:47:00 AM | 104 | DAF | 5.98 | 6.29 | 0.17499999999999999 | 0.32600000000000001 | 87.4 | 5 | - | 0 | 0.28199999999999997 | - | - | - | 40 | 14 min | Alum | 0 | 0.5 | 5 | GAC | Anthracite | 2.2080000000000002
2022-08-25 06:50:00 AM | 104 | F1 | - | 6.24 | 7.4999999999999997E-2 | 0.125 | 92.6 | 1 | - | 0 | 1.7000000000000001E-2 | - | 26.8 | 14.25 | 40 | 14 min | Alum | 0 | 0.5 | 5 | GAC | Anthracite | 1.895
2022-08-25 06:50:59 AM | 104 | F2 | - | 6.26 | 6.7000000000000004E-2 | 0.114 | 90.9 | 1 | - | 0 | 1.2E-2 | - | 58.9 | 8.09 | 40 | 14 min | Alum | 0 | 0.5 | 5 | GAC | Anthracite | 2.0920000000000001
2022-08-25 10:21:00 AM | 105 | Raw | - | 5.75 | 0.26400000000000001 | 0.373 | 77.400000000000006 | 19 | - | 0.02 | 2.9000000000000001E-2 | - | - | - | 40 | 14 min | Alum | 0 | 0.5 | 5 | GAC | Anthracite
2022-08-25 10:23:00 AM | 105 | Rapid Mix | - | 6.38 | - | - | - | - | - | - | - | - | - | - | 40 | 14 min | Alum | 0 | 0.5 | 5 | GAC | Anthracite
2022-08-25 10:21:00 AM | 105 | DAF | 5.98 | 6.32 | 0.182 | 0.33100000000000002 | 87.7 | 5 | - | 0 | 0.29499999999999998 | - | - | - | 40 | 14 min | Alum | 0 | 0.5 | 5 | GAC | Anthracite
2022-08-25 10:22:00 AM | 105 | F1 | - | 6.26 | 7.1999999999999995E-2 | 0.129 | 92.6 | 1 | - | 0 | 1.6E-2 | - | 30.3 | 14.35 | 40 | 14 min | Alum | 0 | 0.5 | 5 | GAC | Anthracite
2022-08-25 10:23:00 AM | 105 | F2 | - | 6.29 | 6.9000000000000006E-2 | 0.111 | 90.8 | 1 | - | 0 | 1.4999999999999999E-2 | - | 62.4 | 8.51 | 40 | 14 min | Alum | 0 | 0.5 | 5 | GAC | Anthracite
2022-08-26 06:14:59 AM | 106 | Raw | - | 5.66 | 0.26300000000000001 | 0.375 | 78.2 | 18 | - | 0.02 | 0.107 | - | - | - | 40 | 14 min | Alum | 0 | 0.5 | 5 | GAC | Anthracite
2022-08-26 06:17:00 AM | 106 | Rapid Mix | - | 6.31 | - | - | - | - | - | - | - | - | - | - | 40 | 14 min | Alum | 0 | 0.5 | 5 | GAC | Anthracite
2022-08-26 06:14:59 AM | 106 | DAF | 5.78 | 6.22 | 0.24199999999999999 | 0.30099999999999999 | 89.4 | 5 | - | 0 | 0.27200000000000002 | - | - | - | 40 | 14 min | Alum | 0 | 0.5 | 5 | GAC | Anthracite
2022-08-26 06:16:00 AM | 106 | F1 | - | 6.19 | 7.4999999999999997E-2 | 0.111 | 94.2 | 1 | - | 0 | 1.7999999999999999E-2 | - | 32.200000000000003 | 15 | 40 | 14 min | Alum | 0 | 0.5 | 5 | GAC | Anthracite
2022-08-26 06:18:00 AM | 106 | F2 | - | 6.22 | 6.2E-2 | 0.107 | 92.2 | 1 | - | 0 | 1.9E-2 | - | 64.3 | 9.42 | 40 | 14 min | Alum | 0 | 0.5 | 5 | GAC | Anthracite
2022-08-29 06:38:00 AM | 107 | Raw | - |  | 0.27100000000000002 | 0.32900000000000001 | 78.2 | 17 | 2.9000000000000001E-2 | 0.02 | 2.9000000000000001E-2 | - | - | - | 40 | 14 min | Alum | 0 | 0.5 | 2 | GAC | Anthracite |  |  | Samples taken for BV Labs
2022-08-29 06:39:00 AM | 107 | Rapid Mix | - | 6.36 | - | - | - | - | - | - | - | - | - | - | 40 | 14 min | Alum | 0 | 0.5 | 2 | GAC | Anthracite
2022-08-29 06:38:00 AM | 107 | DAF |  | 6.28 | 0.245 | 0.30099999999999999 | 88.9 | 6 | 2.3E-2 | 0 | 0.27900000000000003 | - | - | - | 40 | 14 min | Alum | 0 | 0.5 | 2 | GAC | Anthracite |  |  | Samples taken for BV Labs
2022-08-29 06:40:00 AM | 107 | F1 | - | 6.23 | 4.5999999999999999E-2 | 0.108 | 96.1 | 1 | 4.2000000000000003E-2 | 0 | 1.7000000000000001E-2 | - | 1 | 11.63 | 40 | 14 min | Alum | 0 | 0.5 | 2 | GAC | Anthracite |  |  | Samples taken for BV Labs
2022-08-29 06:41:00 AM | 107 | F2 | - |  | 5.5E-2 | 0.112 | 92.1 | 1 | 2.4E-2 | 0 | 2.1999999999999999E-2 | - | 1.5 | 2.09 | 40 | 14 min | Alum | 0 | 0.5 | 2 | GAC | Anthracite |  |  | Samples taken for BV Labs
2022-08-30 07:02:00 AM | 108 | Raw | - | 5.72 | 0.26600000000000001 | 0.33200000000000002 | 78.5 | 16 | 3.2000000000000001E-2 | 0.02 | 2.8000000000000001E-2 | - | - | - | 40 | 14 min | Alum | 0 | 0.5 | 2 | GAC | Anthracite
2022-08-30 07:04:00 AM | 108 | Rapid Mix | - | 6.23 | - | - | - | - | - | - | - | - | - | - | 40 | 14 min | Alum | 0 | 0.5 | 2 | GAC | Anthracite
2022-08-30 07:02:00 AM | 108 | DAF | 6.07 | 6.18 | 0.20100000000000001 | 0.29199999999999998 | 88.9 | 6 | 2.7E-2 | 0 | 0.253 | - | - | - | 40 | 14 min | Alum | 0 | 0.5 | 2 | GAC | Anthracite
2022-08-30 07:05:00 AM | 108 | F1 | - | 6.19 | 4.8000000000000001E-2 | 0.11799999999999999 | 95.3 | 1 | 3.6999999999999998E-2 | 0 | 1.9E-2 | - | 6.4 | 11.44 | 40 | 14 min | Alum | 0 | 0.5 | 2 | GAC | Anthracite
2022-08-30 07:06:00 AM | 108 | F2 | - | 6.21 | 5.8000000000000003E-2 | 0.121 | 91.9 | 1 | 2.7E-2 | 0 | 0.02 | - | 6.9 | 2.0699999999999998 | 40 | 14 min | Alum | 0 | 0.5 | 2 | GAC | Anthracite
2022-08-30 09:33:00 AM | 109 | Raw | - | 5.77 | 2.7E-2 | 0.34100000000000003 | 78.599999999999994 | 17 | - | 0.03 | 3.2000000000000001E-2 | - | - | - | 40 | 14 min | Alum | 0 | 0.5 | 2 | GAC | Anthracite | 3.92
2022-08-30 09:34:00 AM | 109 | Rapid Mix | - | - | - | - | - | - | - | - | - | - | - | - | 40 | 14 min | Alum | 0 | 0.5 | 2 | GAC | Anthracite
2022-08-30 09:33:00 AM | 109 | DAF | 6.08 | 6.25 | 0.189 | 0.30099999999999999 | 89.5 | 6 | - | 0 | 0.26700000000000002 | - | - | - | 40 | 14 min | Alum | 0 | 0.5 | 2 | GAC | Anthracite
2022-08-30 09:35:00 AM | 109 | F1 | - | 6.24 | 5.1999999999999998E-2 | 0.11600000000000001 | 95.2 | 1 | - | 0 | 1.4999999999999999E-2 | - | 8.6 | 11.07 | 40 | 14 min | Alum | 0 | 0.5 | 2 | GAC | Anthracite | 1.4570000000000001
2022-08-30 09:36:00 AM | 109 | F2 | - | 6.26 | 5.8999999999999997E-2 | 0.11899999999999999 | 92.3 | 1 | - | 0 | 1.7000000000000001E-2 | - | 9.1 | 1.92 | 40 | 14 min | Alum | 0 | 0.5 | 2 | GAC | Anthracite | 1.9810000000000001
2022-08-21 05:50:00 AM | 110 | Raw | - | 5.75 | 0.27400000000000002 | 0.32800000000000001 | 78.099999999999994 | 17 | 2.9000000000000001E-2 | 0.03 | 2.9000000000000001E-2 | - | - | - | 40 | 14 min | Alum | 0 | 0.5 | 2 | GAC | Anthracite
2022-08-31 05:53:00 AM | 110 | Rapid Mix | - | 6.31 | - | - | - | - | - | - | - | - | - | - | 40 | 14 min | Alum | 0 | 0.5 | 2 | GAC | Anthracite
2022-08-31 05:52:00 AM | 110 | DAF | 6.05 | 6.3 | 0.16200000000000001 | 0.28499999999999998 | 89.8 | 5 | 2.8000000000000001E-2 | 0 | 0.23400000000000001 | - | - | - | 40 | 14 min | Alum | 0 | 0.5 | 2 | GAC | Anthracite
2022-08-31 05:53:00 AM | 110 | F1 | - | 6.29 | 5.8000000000000003E-2 | 0.106 | 94.4 | 0 | 2.5999999999999999E-2 | 0 | 1.6E-2 | - | 28.5 | 11.65 | 40 | 14 min | Alum | 0 | 0.5 | 2 | GAC | Anthracite
2022-08-31 05:54:00 AM | 110 | F2 | - | 6.31 | 5.8999999999999997E-2 | 0.11700000000000001 | 92.7 | 0 | 2.7E-2 | 0 | 1.0999999999999999E-2 | - | 29 | 2.35 | 40 | 14 min | Alum | 0 | 0.5 | 2 | GAC | Anthracite
2022-08-31 09:22:00 AM | 111 | Raw | - | 5.75 | 0.26500000000000001 | 0.33400000000000002 | 78.099999999999994 | 17 | - | 0.02 | 3.1E-2 | - | - | - | 40 | 14 min | Alum | 0 | 0.5 | 2 | GAC | Anthracite
2022-08-31 09:23:00 AM | 111 | Rapid Mix | - | 6.19 | - | - | - | - | - | - | - | - | - | - | 40 | 14 min | Alum | 0 | 0.5 | 2 | GAC | Anthracite
2022-08-31 09:22:00 AM | 111 | DAF | 5.99 | 6.22 | 0.159 | 0.308 | 89.6 | 4 | - | 0 | 0.245 | - | - | - | 40 | 14 min | Alum | 0 | 0.5 | 2 | GAC | Anthracite
2022-08-31 09:24:00 AM | 111 | F1 | - | 6.2 | 5.8000000000000003E-2 | 0.106 | 93.8 | 0 | - | 0 | 1.4999999999999999E-2 | - | 32.700000000000003 | 11.48 | 40 | 14 min | Alum | 0 | 0.5 | 2 | GAC | Anthracite
2022-08-31 09:25:00 AM | 111 | F2 | - | 6.21 | 5.8000000000000003E-2 | 0.113 | 91.9 | 1 | - | 0 | 1.2E-2 | - | 33.200000000000003 | 2.36 | 40 | 14 min | Alum | 0 | 0.5 | 2 | GAC | Anthracite
2022-09-01 07:03:00 AM | 112 | Raw | - | 5.71 | 0.26700000000000002 | 0.375 | 77.599999999999994 | 17 | 2.8000000000000001E-2 | 0.02 | 2.8000000000000001E-2 | - | - | - | 40 | 14 min | Alum | 0 | 0.5 | 2 | GAC | Anthracite | 3.1259999999999999
2022-09-01 07:04:00 AM | 112 | Rapid Mix | - | 6.18 | - | - | - | - | - | - | - | - | - | - | 40 | 14 min | Alum | 0 | 0.5 | 2 | GAC | Anthracite
2022-09-01 07:03:00 AM | 112 | DAF | 6.12 | 6.16 | 0.214 | 0.28899999999999998 | 89.3 | 6 | 2.3E-2 | 0.01 | 0.25700000000000001 | - | - | - | 40 | 14 min | Alum | 0 | 0.5 | 2 | GAC | Anthracite | 2.274
2022-09-01 07:05:00 AM | 112 | F1 | - | 6.15 | 5.7000000000000002E-2 | 0.113 | 94.8 | 0 | 2.5999999999999999E-2 | 0 | 1.4E-2 | - | 34.4 | 11.82 | 40 | 14 min | Alum | 0 | 0.5 | 2 | GAC | Anthracite | 1.575
2022-09-01 07:06:00 AM | 112 | F2 | - | 6.14 | 5.2999999999999999E-2 | 0.114 | 92.6 | 1 | 2.1999999999999999E-2 | 0 | 1.2E-2 | - | 34.9 | 2.69 | 40 | 14 min | Alum | 0 | 0.5 | 2 | GAC | Anthracite | 1.95
2022-09-07 08:34:00 AM | 113 | Raw | - | 5.66 | 0.311 | 0.41699999999999998 | 78.8 | 17 | 3.1E-2 | 0.03 | 3.4000000000000002E-2 | - | - | - | 40 | 14 min | Alum | 0 | 0.5 | 2 | GAC | Anthracite
2022-09-07 08:36:00 AM | 113 | Rapid Mix | - | 6.31 | - | - | - | - | - | - | - | - | - | - | 40 | 14 min | Alum | 0 | 0.5 | 2 | GAC | Anthracite
2022-09-07 08:35:00 AM | 113 | DAF | 6.1 | 6.26 | 0.23300000000000001 | 0.35899999999999999 | 88.7 | 7 | 2.3E-2 | 0.01 | 0.32500000000000001 | - | - | - | 40 | 14 min | Alum | 0 | 0.5 | 2 | GAC | Anthracite
2022-09-07 08:36:00 AM | 113 | F1 | - | 6.24 | 6.5000000000000002E-2 | 0.13900000000000001 | 95.2 | 0 | 3.5999999999999997E-2 | 0 | 1.2999999999999999E-2 | - | 60.1 | 12.8 | 40 | 14 min | Alum | 0 | 0.5 | 2 | GAC | Anthracite
2022-09-07 08:37:00 AM | 113 | F2 | - | 6.22 | 6.5000000000000002E-2 | 0.13600000000000001 | 92.1 | 1 | 2.3E-2 | 0 | 1.0999999999999999E-2 | - | 60.6 | 3.71 | 40 | 14 min | Alum | 0 | 0.5 | 2 | GAC | Anthracite
2022-09-08 07:15:00 AM | 114 | Raw | - | 5.71 | 0.28899999999999998 | 0.35099999999999998 | 79.3 | 16 | 2.5000000000000001E-2 | 0.03 | 2.9000000000000001E-2 | - | - | - | 40 | 14 min | Alum | 0 | 0.5 | 2 | GAC | Anthracite
2022-09-08 07:16:00 AM | 114 | Rapid Mix | - | 6.29 | - | - | - | - | - | - | - | - | - | - | 40 | 14 min | Alum | 0 | 0.5 | 2 | GAC | Anthracite
2022-09-08 07:15:00 AM | 114 | DAF | 6.26 | 6.27 | 0.217 | 0.30499999999999999 | 88.5 | 6 | 2.3E-2 | 0.01 | 0.309 | - | - | - | 40 | 14 min | Alum | 0 | 0.5 | 2 | GAC | Anthracite
2022-09-08 07:17:00 AM | 114 | F1 | - | 6.24 | 4.4999999999999998E-2 | 0.10100000000000001 | 94.9 | 0 | 0.03 | 0 | 1.4999999999999999E-2 | - | 63.1 | 13.31 | 40 | 14 min | Alum | 0 | 0.5 | 2 | GAC | Anthracite
2022-09-08 07:18:00 AM | 114 | F2 | - | 6.26 | 4.4999999999999998E-2 | 0.112 | 92.3 | 1 | 2.3E-2 | 0 | 1.2999999999999999E-2 | - | 63.6 | 4.01 | 40 | 14 min | Alum | 0 | 0.5 | 2 | GAC | Anthracite
2022-09-09 07:25:00 AM | 115 | Raw | - | 5.84 | 0.28699999999999998 | 0.36199999999999999 | 79.2 | 15 | 2.9000000000000001E-2 | 0.03 | 2.7E-2 | - | - | - | 40 | 14 min | Alum | 0 | 0.5 | 2 | GAC | Anthracite | 3.238
2022-09-09 07:26:00 AM | 115 | Rapid Mix | - | 6.75 | - | - | - | - | - | - | - | - | - | - | 40 | 14 min | Alum | 0 | 0.5 | 2 | GAC | Anthracite
2022-09-09 07:25:00 AM | 115 | DAF | 6.41 | 6.62 | 0.24099999999999999 | 0.32200000000000001 | 88.5 | 5 | 2.4E-2 | 0.01 | 0.315 | - | - | - | 40 | 14 min | Alum | 0 | 0.5 | 2 | GAC | Anthracite | 2.4169999999999998
2022-09-09 07:27:00 AM | 115 | F1 | - | 6.39 | 4.5999999999999999E-2 | 0.11600000000000001 | 94.5 | 0 | 2.4E-2 | 0 | 1.4E-2 | - | 68 | 13.35 | 40 | 14 min | Alum | 0 | 0.5 | 2 | GAC | Anthracite | 1.8460000000000001
2022-09-09 07:28:00 AM | 115 | F2 | - | 6.37 | 5.2999999999999999E-2 | 0.11 | 92.1 | 0 | 2.4E-2 | 0 | 1.2E-2 | - | 68.5 | 4.2699999999999996 | 40 | 14 min | Alum | 0 | 0.5 | 2 | GAC | Anthracite | 2.14
2022-09-16 07:39:00 AM | 116 | Raw | - | 5.79 | 0.41099999999999998 | 0.45500000000000002 | 79.5 | 19 | 3.5000000000000003E-2 | 0.03 | 2.9000000000000001E-2 | - | - | - | 40 | 14 min | Alum | 0 | 0.5 | 2 | GAC | Anthracite
2022-09-16 07:42:00 AM | 116 | Rapid Mix | - | 6.25 | - | - | - | - | - | - | - | - | - | - | 40 | 14 min | Alum | 0 | 0.5 | 2 | GAC | Anthracite
2022-09-06 07:39:00 AM | 116 | DAF | 6 | 6.22 | 0.21099999999999999 | 0.309 | 89.4 | 6 | 2.3E-2 | 0.01 | 0.26400000000000001 | - | - | - | 40 | 14 min | Alum | 0 | 0.5 | 2 | GAC | Anthracite
2022-09-16 07:40:00 AM | 116 | F1 | - | 6.13 | 4.5999999999999999E-2 | 0.111 | 96.3 | 0 | 0.05 | 0 | 1.4999999999999999E-2 | - | 73 | 14.44 | 40 | 14 min | Alum | 0 | 0.5 | 2 | GAC | Anthracite
2022-09-16 07:41:00 AM | 116 | F2 | - | 6.18 | 4.4999999999999998E-2 | 0.11700000000000001 | 92.9 | 1 | 2.4E-2 | 0 | 1.2E-2 | - | 73.5 | 4.7300000000000004 | 40 | 14 min | Alum | 0 | 0.5 | 2 | GAC | Anthracite
2022-09-20 07:26:00 AM | 117 | Raw | - | 5.78 | 0.309 | 0.378 | 80.099999999999994 | 16 | 0.03 | 0.03 | 2.1000000000000001E-2 | - | - | - | 40 | 14 min | Alum | 0 | 0.5 | 2 | GAC | Anthracite | 3 |  | Samples taken for BV Labs
2022-09-20 07:29:00 AM | 117 | Rapid Mix | - | 6.26 | - | - | - | - | - | - | - | - | - | - | 40 | 14 min | Alum | 0 | 0.5 | 2 | GAC | Anthracite
2022-09-20 07:26:00 AM | 117 | DAF | 6.27 | 6.23 | 0.192 | 0.31900000000000001 | 89.6 | 5 | 2.1999999999999999E-2 | 0.01 | 0.27700000000000002 | - | - | - | 40 | 14 min | Alum | 0 | 0.5 | 2 | GAC | Anthracite | 2.2080000000000002 |  | Samples taken for BV Labs
2022-09-20 07:27:00 AM | 117 | F1 | - | 6.17 | 0.04 | 0.11799999999999999 | 95.7 | 1 | 4.1000000000000002E-2 | 0 | 0.01 | - | 76.900000000000006 | 14.49 | 40 | 14 min | Alum | 0 | 0.5 | 2 | GAC | Anthracite | 1.859 |  | Samples taken for BV Labs
2022-09-20 07:28:00 AM | 117 | F2 | - | 6.19 | 3.5999999999999997E-2 | 0.11600000000000001 | 93.4 | 2 | 2.5000000000000001E-2 | 0 | 0.01 | - | 77.400000000000006 | 4.93 | 40 | 14 min | Alum | 0 | 0.5 | 2 | GAC | Anthracite | 1.571 |  | Samples taken for BV Labs
2022-09-21 07:41:00 AM | 118 | Raw | - | 5.75 | 0.30099999999999999 | 0.40500000000000003 | 79.900000000000006 | 16 | 2.7E-2 | 0.03 | 2.4E-2 | - | - | - | 40 | 14 min | Alum | 0 | 0.5 | 2 | GAC | Anthracite |  |  | DBPfp samples @CRWS
2022-09-21 07:42:00 AM | 118 | DAF | 6.22 | 6.24 | 0.20499999999999999 | 0.309 | 89.9 | 5 | 2.1000000000000001E-2 | 0.01 | 0.26200000000000001 | - | - | - | 40 | 14 min | Alum | 0 | 0.5 | 2 | GAC | Anthracite |  |  | DBPfp samples @CWRS
2022-09-21 07:44:00 AM | 118 | F1 | - | 6.18 | 5.2999999999999999E-2 | 0.13300000000000001 | 94.8 | 1 | 2.1999999999999999E-2 | 0 | 1.0999999999999999E-2 | - | 86 | 14.02 | 40 | 14 min | Alum | 0 | 0.5 | 2 | GAC | Anthracite |  |  | DBPfp samples @CWRS
2022-09-21 07:44:59 AM | 118 | F2 | - | 6.17 | 4.8000000000000001E-2 | 0.124 | 92.7 | 2 | 2.4E-2 | 0 | 1.2E-2 | - | 86.5 | 5.12 | 40 | 14 min | Alum | 0 | 0.5 | 2 | GAC | Anthracite |  |  | DBPfp samples @CWRS
2022-09-22 07:51:00 AM | 119 | Raw | - | 5.75 | 0.29599999999999999 | 0.35499999999999998 | 80.099999999999994 | 16 | 2.7E-2 | 0.03 | 2.9000000000000001E-2 | - | - | - | 40 | 7 min | Alum | 0.15 | 0.5 | 2 | GAC | Anthracite
2022-09-22 07:51:00 AM | 119 | DAF | 6.18 | 6.31 | 0.27800000000000002 | 0.41199999999999998 | 88.1 | 9 | 2.8000000000000001E-2 | 0 | 0.35499999999999998 | - | - | - | 40 | 7 min | Alum | 0.15 | 0.5 | 2 | GAC | Anthracite
2022-09-22 07:52:00 AM | 119 | F1 | - | 6.33 | 5.8000000000000003E-2 | 0.11899999999999999 | 95.5 | 0 | 2.5999999999999999E-2 | 0 | 2.8000000000000001E-2 | - | 0.5 | 12.33 | 40 | 7 min | Alum | 0.15 | 0.5 | 2 | GAC | Anthracite
2022-09-22 07:53:00 AM | 119 | F2 | - | 6.38 | 6.6000000000000003E-2 | 0.113 | 93.4 | 0 | 1.6E-2 | 0 | 1.9E-2 | - | 0.9 | 2.38 | 40 | 7 min | Alum | 0.15 | 0.5 | 2 | GAC | Anthracite
2022-09-26 08:41:00 AM | 120 | Raw | - | 7.49 | 0.51200000000000001 | 0.621 | 78.400000000000006 | 24 | - | 0.03 | 0.105 | - | - | - | 40 | 7 min | Alum | 0.15 | 0.5 | 2 | GAC | Anthracite | 2.9020000000000001 |  | DBPfp samples @ CWRS
2022-09-26 08:42:00 AM | 120 | DAF | 5.96 | 6.18 | 0.32700000000000001 | 0.55500000000000005 | 88.4 | 10 | - | 0.01 | 0.36799999999999999 | - | - | - | 40 | 7 min | Alum | 0.15 | 0.5 | 2 | GAC | Anthracite | 2.0950000000000002 |  | DBPfp samples @CWRS
2022-09-26 08:43:00 AM | 120 | F1 | - | 6.17 | 4.1000000000000002E-2 | 0.14899999999999999 | 96 | 2 | - | 0.01 | 8.9999999999999993E-3 | - | 4.2 | 12.21 | 40 | 7 min | Alum | 0.15 | 0.5 | 2 | GAC | Anthracite | TOC @ CWRS |  | DBPfp samples @CWRS
2022-09-26 08:44:00 AM | 120 | F2 | - | 6.22 | 4.3999999999999997E-2 | 0.14599999999999999 | 93.8 | 1 | - | 0 | 1.9E-2 | - | 4.5999999999999996 | 2.33 | 40 | 7 min | Alum | 0.15 | 0.5 | 2 | GAC | Anthracite | TOC @ CWRS |  | DBPfp samples CWRS
2022-09-27 11:56:00 AM | 121 | Raw | - |  | 0.45100000000000001 | 0.495 | 78.5 | 20 | 2.4E-2 | 0.03 | 2.7E-2 | - | - | - | 40 | 7 min | Alum | 0.15 | 0.5 | 2 | GAC | Anthracite | 2.7959999999999998
2022-09-27 11:56:00 AM | 121 | DAF | 6.21 |  | 0.30199999999999999 | 0.47899999999999998 | 87.3 | 10 | 3.1E-2 | 0.01 | 0.32400000000000001 | - | - | - | 40 | 7 min | Alum | 0.15 | 0.5 | 2 | GAC | Anthracite | 2.101
2022-09-27 11:57:00 AM | 121 | F1 | - |  | 6.6000000000000003E-2 | 0.11700000000000001 | 94.6 | 1 | 2.3E-2 | 0 | 1.6E-2 | - | 6 | 12.22 | 40 | 7 min | Alum | 0.15 | 0.5 | 2 | GAC | Anthracite
2022-09-27 11:58:00 AM | 121 | F2 | - |  | 6.9000000000000006E-2 | 0.124 | 92.8 | 2 | 1.6E-2 | 0 | 7.0000000000000001E-3 | - | 6.4 | 2.4500000000000002 | 40 | 7 min | Alum | 0.15 | 0.5 | 2 | GAC | Anthracite
2022-09-28 09:31:00 AM | 122 | Raw | - | 5.75 | 0.42499999999999999 | 0.48599999999999999 | 78.900000000000006 | 20 | - | 0.03 | 2.1999999999999999E-2 | - | - | - | 40 | 7 min | Alum | 0.15 | 0.5 | 2 | GAC | Anthracite
2022-09-28 09:31:00 AM | 122 | DAF | 5.98 | 6.24 | 0.29199999999999998 | 0.47399999999999998 | 88.5 | 11 | - | 0.01 | 0.34300000000000003 | - | - | - | 40 | 7 min | Alum | 0.15 | 0.5 | 2 | GAC | Anthracite
2022-09-28 09:32:00 AM | 122 | F1 | - | 6.17 | 5.3999999999999999E-2 | 0.115 | 95.6 | 2 | - | 0 | 0.02 | - | 11.9 | 12.49 | 40 | 7 min | Alum | 0.15 | 0.5 | 2 | GAC | Anthracite
2022-09-28 09:33:00 AM | 122 | F2 | - | 6.14 | 6.6000000000000003E-2 | 0.124 | 94.1 | 2 | - | 0 | 1.4E-2 | - | 12.3 | 2.72 | 40 | 7 min | Alum | 0.15 | 0.5 | 2 | GAC | Anthracite
2022-09-29 06:48:00 AM | 123 | Raw | - | 5.66 | 0.432 | 0.47499999999999998 | 78.5 | 21 | - | 0.03 | 2.5000000000000001E-2 | - | - | - | 40 | 7 min | Alum | 0.15 | 0.5 | 2 | GAC | Anthracite
2022-09-29 06:48:00 AM | 123 | DAF | 5.94 | 6.09 | 0.16600000000000001 | 0.45900000000000002 | 86.9 | 11 | - | 0.01 | 0.34899999999999998 | - | - | - | 40 | 7 min | Alum | 0.15 | 0.5 | 2 | GAC | Anthracite
2022-09-29 06:49:00 AM | 123 | F1 | - | 6.1 | 6.3E-2 | 0.11700000000000001 | 93.8 | 3 | - | 0.01 | 2.1999999999999999E-2 | - | 33.200000000000003 | 13.35 | 40 | 7 min | Alum | 0.15 | 0.5 | 2 | GAC | Anthracite
2022-09-29 06:50:00 AM | 123 | F2 | - | 6.08 | 5.8999999999999997E-2 | 0.11899999999999999 | 92.8 | 3 | - | 0 | 1.4999999999999999E-2 | - | 33.6 | 3.53 | 40 | 7 min | Alum | 0.15 | 0.5 | 2 | GAC | Anthracite
2022-10-04 07:26:00 AM | 124 | Raw | - | 5.68 | 0.39400000000000002 | 0.48799999999999999 | 78.599999999999994 | 19 | 2.7E-2 | 0.04 | 3.1E-2 | - | - | - | 40 | 7 min | Alum | 0.15 | 0.5 | 2 | GAC | Anthracite | 2.9780000000000002
2022-10-04 07:26:00 AM | 124 | DAF | 5.84 | 6.18 | 0.30599999999999999 | 0.47199999999999998 | 87.5 | 10 | 3.1E-2 | 0.02 | 0.33900000000000002 | - | - | - | 40 | 7 min | Alum | 0.15 | 0.5 | 2 | GAC | Anthracite | 1.8540000000000001
2022-10-04 07:27:00 AM | 124 | F1 | - | 6.14 | 4.3999999999999997E-2 | 0.11899999999999999 | 96.1 | 1 | 3.2000000000000001E-2 | 0.01 | 2.4E-2 | - | 37.1 | 14.06 | 40 | 7 min | Alum | 0.15 | 0.5 | 2 | GAC | Anthracite
2022-10-04 07:28:00 AM | 124 | F2 | - | 6.09 | 4.2999999999999997E-2 | 0.111 | 93.3 | 1 | 2.3E-2 | 0 | 0.01 | - | 37.5 | 4.09 | 40 | 7 min | Alum | 0.15 | 0.5 | 2 | GAC | Anthracite
2022-10-04 10:23:00 AM | 125 | Raw | - | 5.72 | 0.42499999999999999 | 0.47899999999999998 | 78.7 | 20 | - | 0.04 | 0.112 | - | - | - | 40 | 7 min | Alum | 0.15 | 0.5 | 2 | GAC | Anthracite | 2.9580000000000002 | TRUE
2022-10-04 10:26:00 AM | 125 | Rapid Mix | - | 6.21 | - | - | - | - | - | - | - | - | - | - | 40 | 7 min | Alum | 0.15 | 0.5 | 2 | GAC | Anthracite
2022-10-04 10:23:00 AM | 125 | DAF | 5.85 | 6.2 | 0.253 | 0.46400000000000002 | 87.6 | 11 | - | 0.01 | 0.28299999999999997 | - | - | - | 40 | 7 min | Alum | 0.15 | 0.5 | 2 | GAC | Anthracite | 1.9350000000000001 | TRUE
2022-10-04 10:24:00 AM | 125 | F1 | - | 6.19 | 7.4999999999999997E-2 | 0.10100000000000001 | 95.5 | 1 | - | 0 | 2.1999999999999999E-2 | - | 40.299999999999997 | 13.2 | 40 | 7 min | Alum | 0.15 | 0.5 | 2 | GAC | Anthracite |  | TRUE
2022-10-04 10:25:00 AM | 125 | F2 | - | 6.14 | 6.9000000000000006E-2 | 0.105 | 93.4 | 1 | - | 0 | 1.0999999999999999E-2 | - | 40.700000000000003 | 3.78 | 40 | 7 min | Alum | 0.15 | 0.5 | 2 | GAC | Anthracite |  | TRUE
2022-10-05 08:39:00 AM | 126 | Raw | - | 5.74 | 0.39600000000000002 | 0.45600000000000002 | 78.5 | 21 | 0.03 | 0.03 | 4.5999999999999999E-2 | - | - | - | 40 | 7 min | Alum | 0.15 | 0.5 | 2 | GAC | Anthracite
2022-10-05 08:45:00 AM | 126 | Rapid Mix | - | 6.25 | - | - | - | - | - | - | - | - | - | - | 40 | 7 min | Alum | 0.15 | 0.5 | 2 | GAC | Anthracite
2022-10-05 08:39:00 AM | 126 | DAF | 6.32 | 6.22 | 0.23699999999999999 | 0.441 | 87.8 | 11 | 3.5999999999999997E-2 | 0.01 | 0.29799999999999999 | - | - | - | 40 | 7 min | Alum | 0.15 | 0.5 | 2 | GAC | Anthracite
2022-10-05 08:41:00 AM | 126 | F1 | - | 6.24 | 6.7000000000000004E-2 | 0.122 | 94.9 | 2 | 2.7E-2 | 0.01 | 2.1000000000000001E-2 | - | 43.5 | 13.56 | 40 | 7 min | Alum | 0.15 | 0.5 | 2 | GAC | Anthracite
2022-10-05 08:42:00 AM | 126 | F2 | - | 6.23 | 6.3E-2 | 0.115 | 93 | 2 | 2.1999999999999999E-2 | 0 | 1.4E-2 | - | 43.9 | 4.0599999999999996 | 40 | 7 min | Alum | 0.15 | 0.5 | 2 | GAC | Anthracite
2022-10-06 05:52:00 AM | 127 | Raw | - | - | - | 0.41199999999999998 | - | - | - | - | - | - | - | - | 40 | 7 min | Alum | 0.15 | 0.5 | 2 | GAC | Anthracite
2022-10-06 05:52:00 AM | 127 | DAF | 6.15 | - | - | 0.21299999999999999 | - | - | - | - | - | - | - | - | 40 | 7 min | Alum | 0.15 | 0.5 | 2 | GAC | Anthracite
2022-10-06 05:52:00 AM | 127 | F1 | - | - | - | 5.8000000000000003E-2 | - | - | - | - | - | - | 65.3 | 13.25 | 40 | 7 min | Alum | 0.15 | 0.5 | 2 | GAC | Anthracite
2022-10-06 05:52:00 AM | 127 | F2 | - | - | - | 6.3E-2 | - | - | - | - | - | - | 65.7 | 4.75 | 40 | 7 min | Alum | 0.15 | 0.5 | 2 | GAC | Anthracite
2022-10-06 09:42:00 AM | 128 | Raw | - | - | - | 0.42099999999999999 | - | - | - | - | - | - | - | - | 40 | 7 min | Alum | 0.15 | 0.5 | 2 | GAC | Anthracite
2022-10-06 09:42:00 AM | 128 | DAF | 6.05 | - | - | 0.17199999999999999 | - | - | - | - | - | - | - | - | 40 | 7 min | Alum | 0.15 | 0.5 | 2 | GAC | Anthracite
2022-10-06 09:42:00 AM | 128 | F1 | - | - | - | 5.5E-2 | - | - | - | - | - | - | 68.5 | 14.38 | 40 | 7 min | Alum | 0.15 | 0.5 | 2 | GAC | Anthracite
2022-10-06 09:42:00 AM | 128 | F2 | - | - | - | 6.6000000000000003E-2 | - | - | - | - | - | - | 68.900000000000006 | 4.91 | 40 | 7 min | Alum | 0.15 | 0.5 | 2 | GAC | Anthracite
2022-10-11 07:35:00 AM | 129 | Raw | - | 5.69 | 0.34699999999999998 | 0.47699999999999998 | 78.599999999999994 | 20 | 3.1E-2 | 0.03 | 2.8000000000000001E-2 | - | - | - | 40 | 7 min | Alum | 0.15 | 0.5 | 2 | GAC | Anthracite | 2.8050000000000002 | TRUE | 3.9463190173808358
2022-10-11 07:35:59 AM | 129 | DAF | 6.1 | 6.05 | 0.39800000000000002 | 0.49299999999999999 | 87.3 | 10 | 3.6999999999999998E-2 | 0.01 | 0.32700000000000001 | - | - | - | 40 | 7 min | Alum | 0.15 | 0.5 | 2 | GAC | Anthracite | 2.0350000000000001 | TRUE
2022-10-11 07:37:00 AM | 129 | F1 | - | 6.06 | 5.8999999999999997E-2 | 0.11700000000000001 | 95.3 | 1 | 3.2000000000000001E-2 | 0 | 6.0000000000000001E-3 | - | 70.2 | 14.44 | 40 | 7 min | Alum | 0.15 | 0.5 | 2 | GAC | Anthracite | 1.272 | TRUE
2022-10-11 07:38:00 AM | 129 | F2 | - | 6.01 | 4.3999999999999997E-2 | 0.107 | 93.1 | 2 | 2.3E-2 | 0 | 7.0000000000000001E-3 | - | 70.599999999999994 | 5.43 | 40 | 7 min | Alum | 0.15 | 0.5 | 2 | GAC | Anthracite | 1.5880000000000001 | TRUE
2022-10-12 05:31:00 AM | 129 | F1 | - | - | 6.0999999999999999E-2 | 0.122 | - | - | - | - | - | - | 88.4 | 15 | 40 | 7 min | Alum | 0.15 | 0.5 | 2 | GAC | Anthracite
2022-10-12 05:33:00 AM | 129 | F2 | - | - | 5.0999999999999997E-2 | 0.114 | - | - | - | - | - | - | 88.8 | 6.45 | 40 | 7 min | Alum | 0.15 | 0.5 | 2 | GAC | Anthracite
2022-10-13 07:34:00 AM | 130 | Raw | - | 5.71 | 0.32300000000000001 | 0.40300000000000002 | 78.099999999999994 | 20 | 0.03 | 0.03 | 3.5999999999999997E-2 | - | - | - | 50 | 14 min | Alum | 0 | 0.5 | 5 | GAC | Anthracite | 2.8679999999999999 | TRUE | Flo mixer speeds set low (40rpm and 20rpm)
2022-10-13 07:33:00 AM | 130 | DAF | - |  | 0.26700000000000002 | 0.34100000000000003 | 88.8 | 7 | 2.7E-2 | 0.01 | 0.29099999999999998 | - | - | - | 50 | 14 min | Alum | 0 | 0.5 | 5 | GAC | Anthracite | 2.1320000000000001 | TRUE | Flo mixer speeds set low (40rpm and 20rpm)
2022-10-13 10:52:00 AM | 131 | Raw | - | 5.68 | 0.311 | 0.41799999999999998 | 77.8 | 21 | - | 0.03 | 3.5000000000000003E-2 | - | - | - | 50 | 14 min | Alum | 0 | 0.5 | 5 | GAC | Anthracite |  |  | Flo mixer speeds set low (40rpm and 20rpm)
2022-10-13 10:53:00 AM | 131 | DAF | - |  | 0.25600000000000001 | 0.32500000000000001 | 89.1 | 10 | - | 0.01 | 0.25700000000000001 | - | - | - | 50 | 14 min | Alum | 0 | 0.5 | 5 | GAC | Anthracite | 2.0649999999999999 | TRUE | Flo mixer speeds set low (40rpm and 20rpm)
2022-10-14 07:30:00 AM | 132 | Raw | - | 5.56 | 0.309 | 0.442 | 78.599999999999994 | 19 | 3.2000000000000001E-2 | 0.03 |  | - | - | - | 50 | 14 min | Alum | 0 | 0.5 | 5 | GAC | Anthracite | 2.9510000000000001 | TRUE | Flo mixer speeds set high (100rpm and 80rpm)
2022-10-14 07:31:00 AM | 132 | DAF | 6.12 | 5.96 | 0.221 | 0.28399999999999997 | 90.8 | 6 | 2.5000000000000001E-2 | 0 |  | - | - | - | 50 | 14 min | Alum | 0 | 0.5 | 5 | GAC | Anthracite | 1.964 | TRUE | Flo mixer speeds set high (100rpm and 80rpm)
2022-10-14 07:37:00 AM | 133 | Raw | - | 5.59 | 0.312 | 0.40799999999999997 | 78.400000000000006 | 19 | - | 0.03 |  | - | - | - | 50 | 14 min | Alum | 0 | 0.5 | 5 | GAC | Anthracite | 2.9809999999999999 | TRUE | Flo mixer speeds set high (100rpm and 80rpm)
2022-10-14 07:38:00 AM | 133 | DAF | 6.06 | 5.92 | 0.21199999999999999 | 0.28299999999999997 | 90.6 | 6 | - | 0 |  | - | - | - | 50 | 14 min | Alum | 0 | 0.5 | 5 | GAC | Anthracite | 1.8919999999999999 | TRUE | Flo mixer speeds set high (100rpm and 80rpm)
2022-10-19 10:57:00 AM | 134 | Raw | - | 5.81 | 0.23699999999999999 | 0.34799999999999998 | 78.599999999999994 | 18 | 2.9000000000000001E-2 | 0.03 | 4.4999999999999998E-2 | - | - | - | 50 | 14 min | Alum | 0.15 | N/A | 5 | GAC | Anthracite
2022-10-19 10:59:00 AM | 134 | Rapid Mix | - | - | - | - | - | - | - | - | - | - | - | - | 50 | 14 min | Alum | 0.15 | N/A | 5 | GAC | Anthracite
2022-10-19 10:57:00 AM | 134 | DAF | 6.11 | 6.19 | 0.42599999999999999 | 0.46300000000000002 | 89.3 | 10 | 1.9E-2 | 0 | 0.30299999999999999 | - | - | - | 50 | 14 min | Alum | 0.15 | N/A | 5 | GAC | Anthracite
2022-10-19 10:58:00 AM | 134 | F1 | - | 6.11 | 6.5000000000000002E-2 | 0.11600000000000001 | 94.4 | 1 | 1.4E-2 | 0 | 1.2E-2 | - | 2.8 | 13.95 | 50 | 14 min | Alum | 0.15 | N/A | 5 | GAC | Anthracite
2022-10-19 10:59:00 AM | 134 | F2 | - | 6.14 | 0.04 | 0.114 | 93.7 | 2 | 7.0000000000000001E-3 | 0 | 1.0999999999999999E-2 | - | 3.2 | 4.1100000000000003 | 50 | 14 min | Alum | 0.15 | N/A | 5 | GAC | Anthracite
2022-10-20 07:31:00 AM | 135 | Raw | - | 5.78 | 0.21099999999999999 | 0.40799999999999997 | 78.8 | 19 | 2.8000000000000001E-2 | 0.03 | 5.1999999999999998E-2 | - | - | - | 50 | 14 min | Alum | 0.15 | N/A | 5 | GAC | Anthracite | 2.8490000000000002 |  | Samples taken for BV Labs
2022-10-20 07:33:00 AM | 135 | Rapid Mix | - | 9.73 | - | - | - | - | 7.0999999999999994E-2 | - | - | - | - | - | 50 | 14 min | Alum | 0.15 | N/A | 5 | GAC | Anthracite
2022-10-20 07:31:00 AM | 135 | DAF | 6.29 | 6.46 | 0.46700000000000003 | 0.504 | 88.1 | 10 | 0.02 | 0 | 0.27300000000000002 | - | - | - | 50 | 14 min | Alum | 0.15 | N/A | 5 | GAC | Anthracite | 2.024 |  | Samples taken for BV Labs
2022-10-20 07:34:00 AM | 135 | F1 | - | 6.42 | 5.8000000000000003E-2 | 0.11899999999999999 | 94.3 | 2 | 1.2999999999999999E-2 | 0 | 1.4999999999999999E-2 | - | 4.0999999999999996 | 14.17 | 50 | 14 min | Alum | 0.15 | N/A | 5 | GAC | Anthracite | 1.875 |  | Samples taken for BV Labs
2022-10-20 07:35:00 AM | 135 | F2 | - | 6.41 | 4.3999999999999997E-2 | 0.114 | 93.3 | 1 | 4.0000000000000001E-3 | 0 | 8.9999999999999993E-3 | - | 4.5 | 4.51 | 50 | 14 min | Alum | 0.15 | N/A | 5 | GAC | Anthracite | 1.8109999999999999 |  | Samples taken for BV Labs
2022-10-21 06:39:00 AM | 136 | Raw | - | 5.84 | 0.19500000000000001 | 0.42199999999999999 | 79.099999999999994 | 19 | 0.03 | 0.03 | 4.1000000000000002E-2 | - | - | - | 50 | 14 min | Alum | 0.15 | N/A | 5 | GAC | Anthracite | 3.1360000000000001 |  | DBPfp samples @ CWRS
2022-10-21 06:42:00 AM | 136 | Rapid Mix | - | 9.85 | - | - | - | - | - | - | - | - | - | - | 50 | 14 min | Alum | 0.15 | N/A | 5 | GAC | Anthracite
2022-10-21 06:39:00 AM | 136 | DAF | 6.2 | 6.33 | 0.45800000000000002 | 0.52900000000000003 | 89.1 | 11 | 2.1000000000000001E-2 | 0 | 0.249 | - | - | - | 50 | 14 min | Alum | 0.15 | N/A | 5 | GAC | Anthracite | 1.8859999999999999 |  | DBPfp samples @ CWRS
2022-10-21 06:41:00 AM | 136 | F1 | - | 6.26 | 4.7E-2 | 0.123 | 94.7 | 2 | 1.0999999999999999E-2 | 0 | 0.02 | - | 8.4 | 14.58 | 50 | 14 min | Alum | 0.15 | N/A | 5 | GAC | Anthracite | 1.665 |  | DBPfp samples @ CWRS
2022-10-21 06:42:00 AM | 136 | F2 | - | 6.29 | 0.04 | 0.124 | 93.5 | 3 | 6.0000000000000001E-3 | 0 | 5.0000000000000001E-3 | - | 8.8000000000000007 | 4.9400000000000004 | 50 | 14 min | Alum | 0.15 | N/A | 5 | GAC | Anthracite | 1.595 |  | DBPfp samples @ CWRS
2022-10-25 06:30:00 AM | 136 | DAF | - | 6.03 | - | 0.752 | - | - | - | - | - | - | - | - | 30 | 23 min | Alum | 0.15 | 0.5 | 5 | GAC | Anthracite
2022-10-25 07:50:00 AM | 136 | DAF | 6.32 | 6.13 | 0.41099999999999998 | 0.42499999999999999 | 89.1 | 11 | - | - | - | - | - | - | 30 | 23 min | Alum | 0.15 | 0.5 | 5 | GAC | Anthracite
2022-10-25 09:25:00 AM | 137 | Raw | - | 5.82 | 0.33800000000000002 | 0.38500000000000001 | 79.400000000000006 | 18 | 2.9000000000000001E-2 | - | - | - | - | - | 30 | 23 min | Alum | 0.15 | 0.5 | 5 | GAC | Anthracite
2022-10-25 09:26:00 AM | 137 | DAF | 6.28 | 6.19 | 0.39500000000000002 | 0.432 | 89.3 | 10 | 3.3000000000000002E-2 | - | - | - | - | - | 30 | 23 min | Alum | 0.15 | 0.5 | 5 | GAC | Anthracite
2022-10-25 10:15:00 AM | 137 | DAF | 6.26 | 6.21 | 0.376 | 0.41699999999999998 | 89.6 | 9 | 3.1E-2 | - | - | - | - | - | 30 | 23 min | Alum | 0.15 | 0.5 | 5 | GAC | Anthracite
2022-10-25 10:25:00 AM | 137 | DAF | 6.23 | 6.19 | 0.372 | 0.41899999999999998 | 89.4 | 9 | 4.1000000000000002E-2 | - | - | - | - | - | 30 | 23 min | Alum | 0.15 | 0.5 | 5 | GAC | Anthracite
2022-10-27 09:35:00 AM | 138 | Raw | - | 5.84 | 0.32400000000000001 | 0.38500000000000001 | 78.7 | 18 | - | - | - | - | - | - | 30 | 7 min | Alum | 0.15 | 0.5 | 5 | GAC | Anthracite |  |  | DBPfp samples @CWRS
2022-10-27 09:36:00 AM | 138 | DAF | 6.33 | 6.07 | 0.61299999999999999 | 0.77800000000000002 | 85.3 | 13 | - | - | - | - | - | - | 30 | 7 min | Alum | 0.15 | 0.5 | 5 | GAC | Anthracite
2022-10-27 09:42:00 AM | 138 | DAF | 6.31 | 6.08 | 0.61099999999999999 | 0.78400000000000003 | 85.5 | 13 | - | - | - | - | - | - | 30 | 7 min | Alum | 0.15 | 0.5 | 5 | GAC | Anthracite
2022-10-27 10:54:00 AM | 138 | DAF | 6.25 | 6.04 | 0.60399999999999998 | 0.77100000000000002 | 85.2 | 12 | - | - | - | - | - | - | 30 | 7 min | Alum | 0.15 | 0.5 | 5 | GAC | Anthracite | 3.2210000000000001 |  | DBPfp samples @CWRS
2022-10-27 10:55:00 AM | 138 | DAF | 6.23 | 6.04 | 0.59799999999999998 | 0.76100000000000001 | 85.7 | 12 | - | - | - | - | - | - | 30 | 7 min | Alum | 0.15 | 0.5 | 5 | GAC | Anthracite | 2.5219999999999998
2022-10-27 10:56:00 AM | 138 | F1 | - | 5.98 | 6.5000000000000002E-2 | 0.11799999999999999 | 93.8 | 1 | - | - | - | - | 15 | 19.7 | 30 | 7 min | Alum | 0.15 | 0.5 | 5 | GAC | Anthracite |  |  | DBPfp samples @CWRS
2022-10-27 10:57:00 AM | 138 | F2 | - | 5.97 | 4.1000000000000002E-2 | 0.126 | 93 | 2 | - | - | - | - | 5.49 | 20.100000000000001 | 30 | 7 min | Alum | 0.15 | 0.5 | 5 | GAC | Anthracite |  |  | DBPfp samples @CWRS
2022-10-28 08:49:00 AM | 139 | Raw | - | 5.87 | 0.32500000000000001 | 0.39200000000000002 | 78.900000000000006 | 17 | - | - | - | - | - | - | 30 | 14 min | Alum | 0.15 | 0.5 | 5 | GAC | Anthracite | 3.024
2022-10-28 08:51:00 AM | 139 | DAF | 6.46 | 6.23 | 0.46300000000000002 | 0.50600000000000001 | 86.9 | 10 | - | - | - | - | - | - | 30 | 14 min | Alum | 0.15 | 0.5 | 5 | GAC | Anthracite
2022-10-28 08:52:00 AM | 139 | DAF | 6.46 | 6.24 | 0.46200000000000002 | 0.48199999999999998 | 86.9 | 11 | - | - | - | - | - | - | 30 | 14 min | Alum | 0.15 | 0.5 | 5 | GAC | Anthracite | 2.3180000000000001
2022-10-28 08:53:00 AM | 139 | DAF | 6.45 | 6.24 | 0.45900000000000002 | 0.47299999999999998 | 86.7 | 10 | - | - | - | - | - | - | 30 | 14 min | Alum | 0.15 | 0.5 | 5 | GAC | Anthracite | 2.2919999999999998
2022-10-28 08:54:00 AM | 139 | F1 | - | 6.16 | 6.5000000000000002E-2 | 0.108 | 93 | 2 | - | - | - | - | 15 | 24.5 | 30 | 14 min | Alum | 0.15 | 0.5 | 5 | GAC | Anthracite
2022-10-28 08:54:00 AM | 139 | F2 | - | 6.19 | 4.9000000000000002E-2 | 0.106 | 92.3 | 1 | - | - | - | - | 6.34 | 24.9 | 30 | 14 min | Alum | 0.15 | 0.5 | 5 | GAC | Anthracite
2022-11-01 09:22:00 AM | 140 | Raw | - |  | 0.311 | 0.38900000000000001 | 78.900000000000006 | 17 | - | - | 3.1E-2 | - | - | - | 60 | 14 min | Alum | 0.15 | 0.5 | 5 | GAC | Anthracite
2022-11-01 09:22:00 AM | 140 | DAF | 6.5 |  | 0.25900000000000001 | 0.35699999999999998 | 90.1 | 7 | - | - | 0.28000000000000003 | - | - | - | 60 | 14 min | Alum | 0.15 | 0.5 | 5 | GAC | Anthracite | 2.0699999999999998
2022-11-01 09:23:00 AM | 140 | DAF | 6.5 |  | 0.26300000000000001 | 0.34799999999999998 | 89.8 | 7 | - | - | - | - | - | - | 60 | 14 min | Alum | 0.15 | 0.5 | 5 | GAC | Anthracite | 2.0169999999999999
2022-11-01 09:23:00 AM | 140 | DAF | 6.49 |  | 0.25700000000000001 | 0.34200000000000003 | 90 | 6 | - | - | - | - | - | - | 60 | 14 min | Alum | 0.15 | 0.5 | 5 | GAC | Anthracite
2022-11-01 09:24:00 AM | 140 | DAF | 6.49 |  | 0.25800000000000001 | 0.35299999999999998 | 90.1 | 7 | - | - | - | - | - | - | 60 | 14 min | Alum | 0.15 | 0.5 | 5 | GAC | Anthracite
2022-11-01 09:25:00 AM | 140 | F1 | - |  | 4.3999999999999997E-2 | 0.105 | 94.6 | 2 | - | - | 7.0000000000000001E-3 | - | 15 | 28.2 | 60 | 14 min | Alum | 0.15 | 0.5 | 5 | GAC | Anthracite
2022-11-01 09:26:00 AM | 140 | F2 | - |  | 3.9E-2 | 0.10199999999999999 | 94 | 1 | - | - | 6.0000000000000001E-3 | - | 7.55 | 28.6 | 60 | 14 min | Alum | 0.15 | 0.5 | 5 | GAC | Anthracite
2022-11-02 06:32:00 AM | 140 | DAF | 6.5 | 5.97 | 0.26300000000000001 | 0.46700000000000003 | [8 empty] | 70 | 14 min | Alum | 0 | 0.5 | 5 | GAC | Anthracite
2022-11-02 08:42:00 AM | 140 | DAF | 6.42 | 6.01 | 0.22900000000000001 | 0.433 | 88.9 | 9 | - |  |  | - | - | - | 70 | 14 min | Alum | 0 | 0.5 | 5 | GAC | Anthracite
2022-11-02 08:45:00 AM | 140 | DAF | 6.42 | 5.99 | 0.222 | 0.441 | 88.7 | 9 | - | - |  | - | - | - | 70 | 14 min | Alum | 0 | 0.5 | 5 | GAC | Anthracite
2022-11-02 09:22:00 AM | 141 | Raw | - | 5.82 | 0.33400000000000002 | 0.39500000000000002 | 78.099999999999994 | 19 | 0.03 | 0.04 | 3.5000000000000003E-2 | - | - | - | 70 | 14 min | Alum | 0.15 | 0.5 | 5 | GAC | Anthracite
2022-11-02 09:22:00 AM | 141 | DAF | 6.41 | 6.03 | 0.249 | 0.42299999999999999 | 88.7 | 9 | 2.5000000000000001E-2 | 0.01 | - | - | - | - | 70 | 14 min | Alum | 0.15 | 0.5 | 5 | GAC | Anthracite | 2.0139999999999998
2022-11-02 09:23:00 AM | 141 | DAF | 6.41 | 6.02 | 0.24399999999999999 | 0.41899999999999998 | 88.8 | 9 | - | - | - | - | - | - | 70 | 14 min | Alum | 0.15 | 0.5 | 5 | GAC | Anthracite | 1.9930000000000001
2022-11-02 09:25:00 AM | 141 | F1 | - | 5.97 | 5.6000000000000001E-2 | 0.126 | 94.5 | 2 | 2.5000000000000001E-2 | 0 | 3.3000000000000002E-2 | - | 0.9 | 13.39 | 70 | 14 min | Alum | 0.15 | 0.5 | 5 | GAC | Anthracite | 1.4930000000000001
2022-11-02 09:26:00 AM | 141 | F2 | - | 5.98 | 3.9E-2 | 0.106 | 93.6 | 2 | 2.4E-2 | 0 | 1.4E-2 | - | 1.3 | 4.04 | 70 | 14 min | Alum | 0.15 | 0.5 | 5 | GAC | Anthracite | 1.6679999999999999
2022-11-03 04:41:00 AM | 141 | DAF | 6.48 | 6.21 | 0.14199999999999999 | 0.376 | 88.9 | 8 | - | 0.01 | 0.29199999999999998 | - | - | - | 70 | 14 min | Alum | 0 | 0.5 | 5 | GAC | Anthracite
2022-11-03 04:41:00 AM | 141 | DAF | 6.48 | 6.19 | 0.14699999999999999 | 0.36699999999999999 | 89 | 8 | - | - | - | - | - | - | 70 | 14 min | Alum | 0 | 0.5 | 5 | GAC | Anthracite
2022-11-03 04:42:00 AM | 141 | DAF | 6.49 | 6.18 | 0.152 | 0.36299999999999999 | 89.1 | 8 | - | - | - | - | - | - | 70 | 14 min | Alum | 0 | 0.5 | 5 | GAC | Anthracite
2022-11-03 08:28:59 AM | 142 | Raw | - | 5.76 | 0.308 | 0.39800000000000002 | 78.900000000000006 | 17 | 0.03 | 0.04 | 3.2000000000000001E-2 | - | - | - | 70 | 23 min | Alum | 0 | 0.5 | 5 | GAC | Anthracite | 3.0430000000000001
2022-11-03 08:28:59 AM | 142 | DAF | 6.45 | 6.16 | 0.123 | 0.26200000000000001 | 92.2 | 4 | 2.5999999999999999E-2 | 0 | 0.254 | - | - | - | 70 | 23 min | Alum | 0 | 0.5 | 5 | GAC | Anthracite | 1.87
2022-11-03 08:30:00 AM | 142 | DAF | 6.45 | 6.17 | 0.122 | 0.251 | 92 | 4 | - | - | - | - | - | - | 70 | 23 min | Alum | 0 | 0.5 | 5 | GAC | Anthracite | 1.8420000000000001
2022-11-03 08:30:00 AM | 142 | DAF | 6.45 | 6.17 | 0.121 | 0.25600000000000001 | 92 | 5 | - | - | - | - | - | - | 70 | 23 min | Alum | 0 | 0.5 | 5 | GAC | Anthracite
2022-11-03 08:31:00 AM | 142 | DAF | 6.45 | 6.18 | 0.122 | 0.248 | 92.1 | 4 | - | - | - | - | - | - | 70 | 23 min | Alum | 0 | 0.5 | 5 | GAC | Anthracite
2022-11-03 08:32:00 AM | 142 | F1 | - | 6.12 | 5.5E-2 | 0.11600000000000001 | 94.7 | 4 | 2.5999999999999999E-2 | 0 | - | - | 23.8 | 15 | 70 | 23 min | Alum | 0 | 0.5 | 5 | GAC | Anthracite | 1.657
2022-11-03 08:33:00 AM | 142 | F2 | - | 6.14 | 5.0999999999999997E-2 | 0.11799999999999999 | 94.1 | 1 | 2.5999999999999999E-2 | 0 | - | - | 24.3 | 6.62 | 70 | 23 min | Alum | 0 | 0.5 | 5 | GAC | Anthracite | 1.651
2022-11-04 05:25:00 AM | 143 | Raw | - | 5.81 | 0.30499999999999999 | 0.377 | 78.7 | 16 | 2.9000000000000001E-2 | 0.04 | 0.03 | - | - | - | 70 | 23 min | Alum | 0 | 0.5 | 5 | GAC | Anthracite |  |  | Sampled for BV Labs
2022-11-04 05:26:00 AM | 143 | DAF | 6.48 | 6.15 | 9.8000000000000004E-2 | 0.24299999999999999 | 91.7 | 3 | 2.4E-2 | 0 | 0.27700000000000002 | - | - | - | 70 | 23 min | Alum | 0 | 0.5 | 5 | GAC | Anthracite |  |  | Sampled for BV Labs
2022-11-04 05:27:00 AM | 143 | F1 | - | 6.1 | 8.5999999999999993E-2 | 0.13700000000000001 | 94.3 | 1 | 2.5000000000000001E-2 | 0 | 0.09 | - | 44.8 | 15 | 70 | 23 min | Alum | 0 | 0.5 | 5 | GAC | Anthracite |  |  | Sampled for BV Labs
2022-11-04 05:29:00 AM | 143 | F2 | - | 6.11 | 9.4E-2 | 0.14599999999999999 | 93.5 | 1 | 2.5999999999999999E-2 | 0 | 9.2999999999999999E-2 | - | 45.3 | 8.48 | 70 | 23 min | Alum | 0 | 0.5 | 5 | GAC | Anthracite |  |  | Sampled for BV Labs
2022-11-09 08:58:00 AM | 144 | Raw | - | 5.88 | 0.33400000000000002 | 0.40500000000000003 | 78.5 | 17 | - | 0.04 | 0.05 | - | - | - | 80 | 23 min | Alum | 0 | 0.5 | 5 | GAC | Anthracite | 2.9540000000000002
2022-11-09 08:58:00 AM | 144 | DAF | 6.91 | 6.81 | 0.109 | 0.21299999999999999 | 91.1 | 3 | - | 0 | 0.25700000000000001 | - | - | - | 80 | 23 min | Alum | 0 | 0.5 | 5 | GAC | Anthracite
2022-11-09 08:59:00 AM | 144 | DAF | 6.91 | - | 0.111 | 0.20499999999999999 | 91 | 3 | - | - | - | - | - | - | 80 | 23 min | Alum | 0 | 0.5 | 5 | GAC | Anthracite | 1.78
2022-11-09 08:59:00 AM | 144 | DAF | 6.9 | - | 0.108 | 0.21199999999999999 | 91.1 | 4 | - | - | - | - | - | - | 80 | 23 min | Alum | 0 | 0.5 | 5 | GAC | Anthracite | 1.84
2022-11-09 09:01:00 AM | 144 | F1 | - | 6.57 | 5.1999999999999998E-2 | 9.8000000000000004E-2 | 94.2 | 0 | - | 0 | 0.02 | - | 23.9 | 15 | 80 | 23 min | Alum | 0 | 0.5 | 5 | GAC | Anthracite
2022-11-09 09:02:00 AM | 144 | F2 | - | 6.61 | 3.1E-2 | 0.112 | 93.8 | 0 | - | 0 | 3.0000000000000001E-3 | - | 24.3 | 5.55 | 80 | 23 min | Alum | 0 | 0.5 | 5 | GAC | Anthracite
2022-11-10 07:42:00 AM | 145 | Raw | - | 5.83 | 0.34100000000000003 | 0.40100000000000002 | 78.400000000000006 | 17 | - | 0.04 | 5.7000000000000002E-2 | - | - | - | 80 | 23 min | Alum | 0 | 0.5 | 5 | GAC | Anthracite | 2.96
2022-11-10 07:42:00 AM | 145 | DAF | 6.44 | 6.36 | 0.32200000000000001 | 0.216 | 91.8 | 3 | - | 0 | 0.26800000000000002 | - | - | - | 80 | 23 min | Alum | 0 | 0.5 | 5 | GAC | Anthracite | 1.75
2022-11-10 07:44:00 AM | 145 | F1 | - | 6.22 | 7.9000000000000001E-2 | 0.124 | 93.8 | 1 | - | 0 |  | - | 46.8 | 15 | 80 | 23 min | Alum | 0 | 0.5 | 5 | GAC | Anthracite
2022-11-10 07:44:59 AM | 145 | F2 | - | 6.25 | 5.7000000000000002E-2 | 0.153 | 92.6 | 1 | - | 0 | 1.4E-2 | - | 47.2 | 7.01 | 80 | 23 min | Alum | 0 | 0.5 | 5 | GAC | Anthracite
2022-11-15 08:53:00 AM | 146 | Raw | - | 5.75 | 0.30299999999999999 | 0.38300000000000001 | 77.7 | 20 | 3.3000000000000002E-2 | 0.04 | 3.2000000000000001E-2 |  | - | - | 80 | 23 min | Alum | 0 | 0.5 | 5 | GAC | Anthracite
2022-11-15 08:56:00 AM | 146 | Rapid Mix | - | 6.37 | - | - | - | - | - | - | - |  | - | - | 80 | 23 min | Alum | 0 | 0.5 | 5 | GAC | Anthracite
2022-11-15 08:53:00 AM | 146 | DAF | 6.35 | 6.34 | 0.312 | 0.23499999999999999 | 91.1 | 4 | 2.5999999999999999E-2 | 0.01 | 0.27100000000000002 |  | - | - | 80 | 23 min | Alum | 0 | 0.5 | 5 | GAC | Anthracite
2022-11-15 08:55:00 AM | 146 | F1 | - | 6.14 | 7.8E-2 | 0.17799999999999999 | 93.1 | 2 | 2.5999999999999999E-2 | 0 | 6.8000000000000005E-2 |  | 52 | 15 | 80 | 23 min | Alum | 0 | 0.5 | 5 | GAC | Anthracite
2022-11-15 08:56:00 AM | 146 | F2 | - | 6.19 | 6.4000000000000001E-2 | 0.123 | 92.8 | 2 | 2.7E-2 | 0 | 4.2000000000000003E-2 |  | 52.4 | 8.1199999999999992 | 80 | 23 min | Alum | 0 | 0.5 | 5 | GAC | Anthracite
2022-11-16 07:56:00 AM | 147 | Raw | - | 5.76 | 0.33100000000000002 | 0.39200000000000002 | 77.900000000000006 | 20 | - | 0.04 | 3.1E-2 |  | - | - | 80 | 23 min | Alum | 0 | 0.5 | 5 | GAC | Anthracite
2022-11-16 07:56:00 AM | 147 | DAF | 6.49 | 6.45 | 9.6000000000000002E-2 | 0.23599999999999999 | 91.3 | 6 | - | 0.01 | 0.27500000000000002 |  | - | - | 80 | 23 min | Alum | 0 | 0.5 | 5 | GAC | Anthracite
2022-11-16 07:58:00 AM | 147 | F1 | - |  | 0.124 | 0.16800000000000001 | 92.9 | 4 | - | 0 | 0.111 |  | 76.8 | 15 | 80 | 23 min | Alum | 0 | 0.5 | 5 | GAC | Anthracite
2022-11-16 07:58:59 AM | 147 | F2 | - |  | 9.2999999999999999E-2 | 0.17899999999999999 | 92.6 | 5 | - | 0 | 0.13600000000000001 |  | 77.2 | 9.8800000000000008 | 80 | 23 min | Alum | 0 | 0.5 | 5 | GAC | Anthracite
2022-11-18 08:25:00 AM | 148 | Raw | - | 5.82 | 0.35399999999999998 | 0.433 | 77.5 | 21 | 3.5000000000000003E-2 | 0.04 | 2.9000000000000001E-2 |  | - | - | 80 | 14 min | Alum | 0 | 0.5 | 5 | GAC | Anthracite
2022-11-18 08:26:59 AM | 148 | Pre DAF | - | - | - | - | - | - | 3.3000000000000002E-2 | - | - |  | - | - | 80 | 14 min | Alum | 0 | 0.5 | 5 | GAC | Anthracite
2022-11-18 08:25:00 AM | 148 | DAF | 6.17 | 6.34 | 0.14299999999999999 | 0.311 | 90.5 | 8 | 2.9000000000000001E-2 | 0 | - |  | - | - | 80 | 14 min | Alum | 0 | 0.5 | 5 | GAC | Anthracite
2022-11-18 08:47:00 AM | 148 | F1 | - | 6.21 | 6.3E-2 | 0.107 | 94.2 | 2 | 2.7E-2 | 0 | 2.1999999999999999E-2 |  | 0.8 | 14.81 | 80 | 14 min | Alum | 0 | 0.5 | 5 | GAC | Anthracite
2022-11-18 08:26:00 AM | 148 | F2 | - | 6.23 | 4.1000000000000002E-2 | 0.111 | 93.9 | 3 | 2.9000000000000001E-2 | 0 | 1.7999999999999999E-2 |  | 0.8 | 4.8099999999999996 | 80 | 14 min | Alum | 0 | 0.5 | 5 | GAC | Anthracite
2022-11-22 09:50:59 AM | 149 | Raw | - | 5.83 | 0.31900000000000001 | 0.39100000000000001 | 77.099999999999994 | 20 | - | 0.03 | 4.7E-2 |  | - | - | 80 | 14 min | Alum | 0 | 0.5 | 5 | GAC | Anthracite
2022-11-22 09:51:59 AM | 149 | DAF | 6.09 | 5.82 | 0.112 | 0.32600000000000001 | 90.1 | 6 | - | 0 | 0.29299999999999998 |  | - | - | 80 | 14 min | Alum | 0 | 0.5 | 5 | GAC | Anthracite
2022-11-23 05:52:00 AM | 150 | Raw | - | 5.81 | 0.31900000000000001 | 0.41 | 77.599999999999994 | 20 | 3.3000000000000002E-2 | 0.04 | 3.7999999999999999E-2 |  | - | - | 80 | 14 min | Alum | 0 | 0.5 | 5 | GAC | Anthracite |  |  | DBPfp samples @CWRS
2022-11-23 05:53:00 AM | 150 | DAF | 6.27 | 5.65 | 0.108 | 0.441 | 90.8 | 5 | 2.8000000000000001E-2 | 0.01 | 0.30599999999999999 |  | - | - | 80 | 14 min | Alum | 0 | 0.5 | 5 | GAC | Anthracite |  |  | DBPfp samples @CWRS
2022-11-24 09:44:59 AM | 151 | Raw | - | 5.85 | 0.32700000000000001 | 0.39100000000000001 | 71.099999999999994 | 20 | - | 0.04 | - |  | - | - | 80 | 7 min | Alum | 0 | 0.5 | 5 | GAC | Anthracite
2022-11-24 09:47:00 AM | 151 | DAF | - | 6.12 | 0.315 | 0.41699999999999998 | 86.6 | 12 | - | 0.01 | - |  | - | - | 80 | 7 min | Alum | 0 | 0.5 | 5 | GAC | Anthracite
2022-11-29 08:31:00 AM | 152 | Raw | - | 5.75 | 0.32900000000000001 | 0.42099999999999999 | 75.900000000000006 | 21 | 3.5999999999999997E-2 | 0.05 | 1.9E-2 |  | - | - | 60 | 7 min | Alum | 0 | 0.5 | 5 | GAC | Anthracite | TOC @ CWRS
2022-11-29 08:32:00 AM | 152 | DAF | - | 6.21 | 0.309 | 0.47199999999999998 | 86.2 | 11 | 3.1E-2 | 0.01 | 0.40600000000000003 |  | - | - | 60 | 7 min | Alum | 0 | 0.5 | 5 | GAC | Anthracite | TOC @ CWRS
2022-11-30 09:10:00 AM | 153 | Raw | - | 5.85 | 0.34499999999999997 | 0.98099999999999998 | 77.099999999999994 | 20 | 3.4000000000000002E-2 | 0.05 | 3.7999999999999999E-2 |  | - | - | 60 | 7 min | Alum | 0 | 0.5 | 5 | GAC | Anthracite
2022-11-30 09:15:00 AM | 153 | DAF | 5.95 | 6.34 | 0.19800000000000001 | 0.76500000000000001 | 87.2 | 12 | 0.03 | 0.01 | 0.36599999999999999 |  | - | - | 60 | 7 min | Alum | 0 | 0.5 | 5 | GAC | Anthracite
2022-12-01 05:20:59 AM | 154 | Raw | - | 5.75 | 0.38300000000000001 | 0.438 | 76.5 | 21 | - | 0.04 | 1.7000000000000001E-2 |  | - | - | 60 | 7 min | Alum | 0 | 0.5 | 5 | GAC | Anthracite | TOC @ CWRS
2022-12-01 05:22:00 AM | 154 | DAF | 6.41 | 6.06 | 0.13600000000000001 | 0.42299999999999999 | 86.9 | 11 | - | 0.02 | 0.27100000000000002 |  | - | - | 60 | 7 min | Alum | 0 | 0.5 | 5 | GAC | Anthracite | TOC @ CWRS
2022-12-02 08:30:00 AM | 155 | Raw | - | 5.78 | 0.35299999999999998 | 0.441 | 76.900000000000006 |  | 3.5999999999999997E-2 | - | 4.9000000000000002E-2 |  | - | - | 60 | 29 min | Alum | 0.15 | 2/3 minutes | 5 | GAC | Anthracite
2022-12-02 08:31:00 AM | 155 | DAF | 5.89 | 5.79 | 0.106 | 0.502 | 91.1 |  | 2.5999999999999999E-2 | - | 0.28399999999999997 |  | - | - | 60 | 29 min | Alum | 0.15 | 2/3 minutes | 5 | GAC | Anthracite
2022-12-05 09:34:00 AM | 156 | Raw | - | 5.79 | 0.375 | 0.44900000000000001 | 76.5 | 22 | 3.4000000000000002E-2 | 0.04 | 6.5000000000000002E-2 |  | - | - | 60 | 18 min | Alum | 0.15 | 2/3 minutes | 2 | GAC | Anthracite
2022-12-05 09:35:00 AM | 156 | DAF | 5.91 | 6.18 | 0.41 | 0 | 86.1 | 14 | 3.7999999999999999E-2 | 0.01 | 0.39100000000000001 |  | - | - | 60 | 18 min | Alum | 0.15 | 2/3 minutes | 2 | GAC | Anthracite
2022-12-09 09:25:00 AM | 157 | Raw | - | 5.91 | 0.371 | 0.59199999999999997 | 75.599999999999994 | 24 | 3.5999999999999997E-2 | - | - |  | - | - | 54 | 18 min | Alum | 0.15 | 2/3 minutes | 2 | GAC | Anthracite
2022-12-09 09:26:00 AM | 157 | DAF | 6.18 | 7.09 | 0.94299999999999995 | 0.97599999999999998 | 81.599999999999994 | 21 | 3.9E-2 | - | - |  | - | - | 54 | 18 min | Alum | 0.15 | 2/3 minutes | 2 | GAC | Anthracite
2022-12-09 09:28:00 AM | 157 | F1 | - | 6.73 | - | 0.86 | 79.099999999999994 | 22 | 6.3E-2 | - | - |  | 3.7 | 14.41 | 54 | 18 min | Alum | 0.15 | 2/3 minutes | 2 | GAC | Anthracite
2022-12-09 09:29:00 AM | 157 | F2 | - | 7.23 | - | 0.99299999999999999 | 71.8 | 30 | 6.2E-2 | - | - |  | 4.0999999999999996 | 3.57 | 54 | 18 min | Alum | 0.15 | 2/3 minutes | 2 | GAC | Anthracite
2022-12-16 09:15:00 PM | 158 | Raw | - | 5.76 | 0.30299999999999999 | 0.48199999999999998 | 75.2 | 23 | - | 0.06 | 7.0999999999999994E-2 |  | - | - | 54 | 11 min | Alum | 0 | 0.5 | 2 | GAC | Anthracite
2022-12-16 07:16:00 AM | 158 | DAF | 6.27 | 6.18 | 0.504 | 0.66200000000000003 | 84.4 | 14 | - | 0.03 | 0.36199999999999999 |  | - | - | 54 | 11 min | Alum | 0 | 0.5 | 2 | GAC | Anthracite
2022-12-16 07:18:00 AM | 158 | F1 | - |  | 4.8000000000000001E-2 | 0.14699999999999999 | 94.3 | 5 | - | 0.01 | 1.4999999999999999E-2 |  | 6.7 | 14.51 | 54 | 11 min | Alum | 0 | 0.5 | 2 | GAC | Anthracite
2022-12-16 07:20:00 AM | 158 | F2 | - |  | 5.1999999999999998E-2 | 0.11700000000000001 | 92.8 | 5 | - | 0.01 | 2.1000000000000001E-2 |  | 7.1 | 3.72 | 54 | 11 min | Alum | 0 | 0.5 | 2 | GAC | Anthracite
2022-12-19 07:56:00 AM | 159 | Raw | - | 5.95 | 0.27600000000000002 | 0.46200000000000002 | 76.2 | 22 | - | 0.06 | 2.4E-2 |  | - | - | 54 | 11 min | Alum | 0 | 0.5 | 2 | GAC | Anthracite
2022-12-19 07:56:59 AM | 159 | DAF | 6.08 | 6.73 | 0.498 | 0.73199999999999998 | 81.900000000000006 | 18 | - | 0.03 | 0.252 |  | - | - | 54 | 11 min | Alum | 0 | 0.5 | 2 | GAC | Anthracite
2022-12-19 07:58:59 AM | 159 | F1 | - | 6.61 | 0.05 | 0.153 | 94.6 | 1 | - | 0.01 | 3.4000000000000002E-2 |  | 9.6 | 15 | 54 | 11 min | Alum | 0 | 0.5 | 2 | GAC | Anthracite
2022-12-19 08:01:00 AM | 159 | F2 | - | 6.68 | 4.3999999999999997E-2 | 0.11799999999999999 | 92.4 | 1 | - | 0 | 0.02 |  | 10 | 4.38 | 54 | 11 min | Alum | 0 | 0.5 | 2 | GAC | Anthracite
2022-12-20 05:56:00 AM | 160 | Raw | - | 5.94 | 0.27200000000000002 | 0.44400000000000001 | 75.2 | 24 | 3.2000000000000001E-2 | 0.03 | 0.02 |  | - | - | 54 | 11 min | Alum | 0 | 0.5 | 2 | GAC | Anthracite
2022-12-20 05:57:00 AM | 160 | DAF | 6.77 | 6.82 | 0.215 | 0.435 | 86.8 | 11 | 2.8000000000000001E-2 | 0.01 | 0.30399999999999999 |  | - | - | 54 | 11 min | Alum | 0 | 0.5 | 2 | GAC | Anthracite
2022-12-20 05:59:00 AM | 160 | F1 | - | 6.73 | 4.2000000000000003E-2 | 0.11600000000000001 | 93.4 | 4 | 2.4E-2 | 0 | 1.2999999999999999E-2 |  | 31.7 | 15 | 54 | 11 min | Alum | 0 | 0.5 | 2 | GAC | Anthracite
2022-12-20 06:01:00 AM | 160 | F2 | - | 6.78 | 3.3000000000000002E-2 | 0.10100000000000001 | 92.4 | 4 | 2.8000000000000001E-2 | 0 | 1.4999999999999999E-2 |  | 32.1 | 5.38 | 54 | 11 min | Alum | 0 | 0.5 | 2 | GAC | Anthracite
2023-01-13 06:04:00 AM | 161 | Raw |  | 5.58 | 0.35799999999999998 | 0.46300000000000002 | 74.8 | 24 |  | 0.05 | 3.9E-2 |  |  |  | 60 | 24 min | Alum | 0 |  | 2 | GAC | Anthracite
2023-01-13 06:05:59 AM | 161 | DAF | 6.3 | 5.93 | 0.22800000000000001 | 0.39300000000000002 | 89.6 | 10 |  | 0.01 | 0.28299999999999997 |  |  |  | 60 | 24 min | Alum | 0 |  | 2 | GAC | Anthracite
2023-01-13 06:08:00 AM | 161 | F1 |  | 5.82 | 0.18099999999999999 | 0.216 | 93.5 | 4 |  | 0.01 | 4.2999999999999997E-2 |  | 1.4 | 14.54 | 60 | 24 min | Alum | 0 |  | 2 | GAC | Anthracite
2023-01-13 06:11:00 AM | 161 | F2 |  | 5.97 | 0.17899999999999999 | 0.27100000000000002 | 88.6 | 7 |  | 0.01 | 9.6000000000000002E-2 |  | 1 | 4.34 | 60 | 24 min | Alum | 0 |  | 2 | GAC | Anthracite
2023-01-13 09:03:59 AM | 162 | Raw |  | 5.37 | 0.35599999999999998 | 0.48299999999999998 | 74.400000000000006 | 24 | [6 empty] | 60 | 21 min | Alum | 0 |  | 2 | GAC | Anthracite | TOC @ CWRS
2023-01-13 09:05:00 AM | 162 | DAF | 6.45 | 6.04 | 0.224 | 0.55700000000000005 | 87.4 | 10 | [6 empty] | 60 | 21 min | Alum | 0 |  | 2 | GAC | Anthracite | TOC @ CWRS
2023-01-13 09:06:59 AM | 162 | F1 |  | 5.97 | 5.5E-2 | 0.122 | 95.1 | 1 |  |  | 1.2E-2 |  | 4 | 14.62 | 60 | 21 min | Alum | 0 |  | 2 | GAC | Anthracite | TOC @ CWRS
2023-01-13 09:07:59 AM | 162 | F2 |  | 5.89 | 3.2000000000000001E-2 | 0.151 | 94 | 2 |  |  | 5.0000000000000001E-3 |  | 3.6 | 4.41 | 60 | 21 min | Alum | 0 |  | 2 | GAC | Anthracite | TOC @ CWRS
2023-01-16 06:40:00 AM | 163 | Raw |  |  | 0.98399999999999999 | 1.04 | 72.5 | 31 | [6 empty] | 60 | 21 min | Alum | 0 |  | 2 | GAC | Anthracite
2023-01-16 10:05:00 AM | 164 | Raw |  | 5.36 | 0.86699999999999999 | 0.878 | 73 | 30 |  | 0.05 | 3.3000000000000002E-2 |  |  |  | 68 | 21 min | Alum | 0 |  | 2 | GAC | Anthracite
2023-01-16 10:06:00 AM | 164 | DAF | 6.57 | 6.23 | 0.55400000000000005 | 1.0900000000000001 | 81.099999999999994 | 25 |  | 0.02 | 0.32400000000000001 |  |  |  | 68 | 21 min | Alum | 0 |  | 2 | GAC | Anthracite
2023-01-16 10:08:00 AM | 164 | F1 |  | 5.93 | 4.3999999999999997E-2 | 0.13600000000000001 | 95.3 | 1 |  | 0.01 | 2E-3 |  | 6.4 | 13.98 | 68 | 21 min | Alum | 0 |  | 2 | GAC | Anthracite
2023-01-16 10:09:00 AM | 164 | F2 |  | 5.86 | 3.4000000000000002E-2 | 0.158 | 93.6 | 1 |  | 0.01 | 4.0000000000000001E-3 |  | 6 | 4.78 | 68 | 21 min | Alum | 0 |  | 2 | GAC | Anthracite
2023-01-17 07:08:00 AM | 165 | Raw |  | 5.43 | 0.42399999999999999 | 0.53600000000000003 | 73.3 | 26 |  | 0.04 | 4.8000000000000001E-2 |  |  |  | 44 | 21 min | Alum | 0 |  | 2 | GAC | Anthracite
2023-01-17 07:09:59 AM | 165 | DAF | 6.57 | 6.07 | 0.434 | 0.80800000000000005 | 81.5 | 22 |  | 0.02 | 0.26800000000000002 |  |  |  | 44 | 21 min | Alum | 0 |  | 2 | GAC | Anthracite
2023-01-17 07:11:59 AM | 165 | F1 |  | 5.99 | 4.9000000000000002E-2 | 0.115 | 94.7 | 1 |  | 0.01 | 7.0000000000000001E-3 |  | 9.1999999999999993 | 14.54 | 44 | 21 min | Alum | 0 |  | 2 | GAC | Anthracite
2023-01-17 07:13:59 AM | 165 | F2 |  | 5.94 | 3.3000000000000002E-2 | 0.13800000000000001 | 93.4 | 1 |  | 0.01 | 4.0000000000000001E-3 |  | 8.8000000000000007 | 4.8099999999999996 | 44 | 21 min | Alum | 0 |  | 2 | GAC | Anthracite
2023-01-17 10:27:00 AM | 166 | Raw |  | 5.55 | 0.42099999999999999 | 0.52800000000000002 | 73.3 | 25 | [6 empty] | 60 | 21 min | Alum | 0 |  | 2 | GAC | Anthracite
2023-01-17 10:28:00 AM | 166 | DAF | 6.77 | 6.37 | 0.35699999999999998 | 0.70699999999999996 | 84.3 | 15 | [6 empty] | 60 | 21 min | Alum | 0 |  | 2 | GAC | Anthracite
2023-01-17 10:29:00 AM | 166 | F1 |  | 6.19 | 4.9000000000000002E-2 | 0.125 | 94.4 | 1 |  |  |  |  | 12 | 15 | 60 | 21 min | Alum | 0 |  | 2 | GAC | Anthracite
2023-01-17 10:31:00 AM | 166 | F2 |  | 6.18 | 3.5999999999999997E-2 | 0.111 | 93.4 | 1 |  |  |  |  | 11.6 | 5.17 | 60 | 21 min | Alum | 0 |  | 2 | GAC | Anthracite
2023-01-18 07:04:00 AM | 167 | Raw |  | 5.44 | 0.38700000000000001 | 0.47499999999999998 | 73.599999999999994 | 24 |  | 0.05 | 3.5000000000000003E-2 |  |  |  | 68 | 21 min | Alum | 0 |  | 2 | GAC | Anthracite
2023-01-18 07:05:00 AM | 167 | DAF | 6.58 | 6.41 | 0.30299999999999999 | 0.501 | 87.1 | 12 |  | 0.01 | 0.25600000000000001 |  |  |  | 68 | 21 min | Alum | 0 |  | 2 | GAC | Anthracite
2023-01-18 07:07:00 AM | 167 | F1 |  | 6.07 | 4.7E-2 | 0.126 | 94.9 | 1 |  | 0.01 | 4.0000000000000001E-3 |  | 14.7 | 15 | 68 | 21 min | Alum | 0 |  | 2 | GAC | Anthracite
2023-01-18 07:08:00 AM | 167 | F2 |  | 6.01 | 0.03 | 0.158 | 93.5 | 2 |  | 0.01 | 1E-3 |  | 14.3 | 5.45 | 68 | 21 min | Alum | 0 |  | 2 | GAC | Anthracite
2023-01-18 08:53:00 AM | 168 | Raw |  | 5.45 | 0.378 | 0.47 | 73.900000000000006 | 25 | [6 empty] | 76 | 21 min | Alum | 0 |  | 2 | GAC | Anthracite | TOC @ CWRS
2023-01-18 08:54:00 AM | 168 | DAF | 6.63 | 6.02 | 0.26800000000000002 | 0.35799999999999998 | 89.8 | 8 | 2.5000000000000001E-2 | [5 empty] | 76 | 21 min | Alum | 0 |  | 2 | GAC | Anthracite | TOC @ CWRS
2023-01-18 08:56:00 AM | 168 | F1 |  | 5.98 | 3.7999999999999999E-2 | 0.10299999999999999 | 95.2 | 1 | 2.5999999999999999E-2 |  |  |  | 16.399999999999999 | 15 | 76 | 21 min | Alum | 0 |  | 2 | GAC | Anthracite | TOC @ CWRS
2023-01-18 08:57:00 AM | 168 | F2 |  | 6.03 | 3.1E-2 | 0.155 | 94.3 | 1 | 2.3E-2 |  |  |  | 16 | 5.58 | 76 | 21 min | Alum | 0 |  | 2 | GAC | Anthracite | TOC @ CWRS
2023-01-19 08:59:00 AM | 169 | Raw |  | 5.45 | 0.39700000000000002 | 0.48299999999999998 | 73.7 | 23 | [6 empty] | 76 | 14 min | Alum | 0 |  | 2 | GAC | Anthracite
2023-01-19 08:59:59 AM | 169 | DAF | 6.28 | 5.73 | 0.41 | 0.56999999999999995 | 85.9 | 10 | [6 empty] | 76 | 14 min | Alum | 0 |  | 2 | GAC | Anthracite
2023-01-19 09:03:00 AM | 169 | F1 |  | 5.95 | 4.4999999999999998E-2 | 0.107 | 95 | 1 |  |  |  |  | 21.6 | 14.1 | 76 | 14 min | Alum | 0 |  | 2 | GAC | Anthracite
2023-01-19 09:03:59 AM | 169 | F2 |  | 5.82 | 0.04 | 0.14899999999999999 | 94.1 | 2 |  |  |  |  | 21.2 | 4.72 | 76 | 14 min | Alum | 0 |  | 2 | GAC | Anthracite
2023-01-20 10:20:00 AM | 170 | Raw |  | 5.62 | 0.39100000000000001 | 0.48099999999999998 | 74 | 24 |  | 0.05 | 5.0999999999999997E-2 |  |  |  | 84 | 14 min | Alum | 0 |  | 2 | GAC | Anthracite
2023-01-20 10:21:00 AM | 170 | DAF | 6.74 | 6.67 | 0.32600000000000001 | 0.61499999999999999 | 86 | 15 |  | 0.02 | 0.33900000000000002 |  |  |  | 84 | 14 min | Alum | 0 |  | 2 | GAC | Anthracite
2023-01-20 10:23:00 AM | 170 | F1 |  | 6.4 | 0.10199999999999999 | 0.158 | 94.8 | 4 |  | 0.01 | 7.4999999999999997E-2 |  | 26.8 | 15 | 84 | 14 min | Alum | 0 |  | 2 | GAC | Anthracite
2023-01-20 10:24:00 AM | 170 | F2 |  | 6.2 | 9.2999999999999999E-2 | 0.17399999999999999 | 93.3 | 5 |  | 0.01 | 8.5000000000000006E-2 |  | 26.4 | 6.78 | 84 | 14 min | Alum | 0 |  | 2 | GAC | Anthracite
2023-01-23 07:03:00 AM | 171 | Raw |  | 5.43 | 0.4 | 0.49 | 73.099999999999994 | 25 |  | 0.05 |  |  |  |  | 84 | 14 min | Alum | 0 |  | 2 | GAC | Anthracite | TOC @ CWRS
2023-01-23 07:04:00 AM | 171 | DAF | 6.7 | 5.95 | 0.27300000000000002 | 0.41799999999999998 | 88.3 | 10 |  | 0.01 |  |  |  |  | 84 | 14 min | Alum | 0 |  | 2 | GAC | Anthracite | TOC @ CWRS
2023-01-23 07:07:00 AM | 171 | F1 |  | 5.86 | 0.08 | 0.153 | 94.7 | 2 |  | 0.01 |  |  | 29.3 | 15 | 84 | 14 min | Alum | 0 |  | 2 | GAC | Anthracite | TOC @ CWRS
2023-01-23 07:08:00 AM | 171 | F2 |  | 5.79 | 7.0000000000000007E-2 | 0.17299999999999999 | 93.5 | 2 |  | 0.01 |  |  | 28.9 | 8.35 | 84 | 14 min | Alum | 0 |  | 2 | GAC | Anthracite | TOC @ CWRS
2023-01-23 11:02:00 AM | 172 | Raw |  | 5.35 | 0.40799999999999997 | 0.50800000000000001 | 73.400000000000006 | 25 | [6 empty] | 84 | 14 min | Alum | 0 |  | 2 | GAC | Anthracite
2023-01-23 11:03:00 AM | 172 | DAF | 6.72 | 5.99 | 0.28699999999999998 | 0.47799999999999998 | 88.1 | 10 | [6 empty] | 84 | 14 min | Alum | 0 |  | 2 | GAC | Anthracite
2023-01-23 11:05:00 AM | 172 | F1 |  | 5.9 | 0.13500000000000001 | 0.20499999999999999 | 94.2 | 2 |  |  |  |  | 31.3 | 15 | 84 | 14 min | Alum | 0 |  | 2 | GAC | Anthracite
2023-01-23 11:06:00 AM | 172 | F2 |  | 5.82 | 0.10100000000000001 | 0.17100000000000001 | 93.3 | 3 |  |  |  |  | 30.9 | 9.01 | 84 | 14 min | Alum | 0 |  | 2 | GAC | Anthracite
2023-01-24 09:44:59 AM | 173 | Raw |  | 5.55 | 0.59499999999999997 | 0.63300000000000001 | 73 | 28 |  | 0.05 |  |  |  |  | 76 | 14 min | Alum | 0 |  | 2 | GAC | Anthracite | TOC @ CWRS
2023-01-24 09:46:00 AM | 173 | DAF | 6.58 | 6.23 | 0.317 | 0.54300000000000004 | 88.2 | 11 |  | 0.02 |  |  |  |  | 76 | 14 min | Alum | 0 |  | 2 | GAC | Anthracite | TOC @ CWRS
2023-01-24 09:47:00 AM | 173 | F1 |  | 6.03 | 0.114 | 0.184 | 94.3 | 2 |  | 0.01 |  |  | 33.200000000000003 | 14.27 | 76 | 14 min | Alum | 0 |  | 2 | GAC | Anthracite | TOC @ CWRS
2023-01-24 09:48:00 AM | 173 | F2 |  | 5.94 | 8.3000000000000004E-2 | 0.16300000000000001 | 93.5 | 3 |  | 0.01 |  |  | 32.799999999999997 | 9.2899999999999991 | 76 | 14 min | Alum | 0 |  | 2 | GAC | Anthracite | TOC @ CWRS
2023-01-24 11:04:00 AM | 174 | Raw |  | 5.4 | 0.65400000000000003 | 0.70399999999999996 | 72.900000000000006 | 27 | [6 empty] | 76 | 14 min | Alum | 0 |  | 2 | GAC | Anthracite
2023-01-24 11:05:00 AM | 174 | DAF | 6.6 | 6.04 | 0.312 | 0.47499999999999998 | 88.3 | 9 | 2.8000000000000001E-2 | [5 empty] | 76 | 14 min | Alum | 0 |  | 2 | GAC | Anthracite
2023-01-24 11:08:00 AM | 174 | F1 |  | 5.95 | 0.111 | 0.16700000000000001 | 94.6 | 2 | 2.8000000000000001E-2 |  |  |  | 34.5 | 14.41 | 76 | 14 min | Alum | 0 |  | 2 | GAC | Anthracite
2023-01-24 11:09:00 AM | 174 | F2 |  | 5.83 | 7.0000000000000007E-2 | 0.13900000000000001 | 94 | 1 | 0.03 |  |  |  | 34.1 | 8.6 | 76 | 14 min | Alum | 0 |  | 2 | GAC | Anthracite
2023-01-25 07:25:00 AM | 175 | Raw |  | 5.59 | 0.501 | 0.56499999999999995 | 73 | 25 |  | 0.06 |  |  |  |  | 68 | 14 min | Alum | 0 |  | 2 | GAC | Anthracite
2023-01-25 07:26:00 AM | 175 | DAF | 6.55 | 5.94 | 0.50600000000000001 | 0.64200000000000002 | 84.8 | 14 |  | 0.03 |  |  |  |  | 68 | 14 min | Alum | 0 |  | 2 | GAC | Anthracite
2023-01-25 07:29:00 AM | 175 | F1 |  | 6.11 | 7.5999999999999998E-2 | 0.13900000000000001 | 94.8 | 2 |  | 0.01 |  |  | 36.6 | 15 | 68 | 14 min | Alum | 0 |  | 2 | GAC | Anthracite
2023-01-25 07:30:00 AM | 175 | F2 |  | 5.98 | 5.5E-2 | 0.13 | 94 | 2 |  | 0.01 |  |  | 36.200000000000003 | 9.4600000000000009 | 68 | 14 min | Alum | 0 |  | 2 | GAC | Anthracite
2023-01-25 10:08:00 AM | 176 | Raw |  | 5.66 | 0.48699999999999999 | 0.56200000000000006 | 73.3 | 25 | [6 empty] | 68 | 14 min | Alum | 0 |  | 2 | GAC | Anthracite | TOC @ CWRS
2023-01-25 10:09:00 AM | 176 | DAF | 6.59 | 6.04 | 0.42899999999999999 | 0.58299999999999996 | 85.7 | 12 | 3.2000000000000001E-2 | [5 empty] | 68 | 14 min | Alum | 0 |  | 2 | GAC | Anthracite | TOC @ CWRS
2023-01-25 10:11:00 AM | 176 | F1 |  | 6.14 | 0.14499999999999999 | 0.19400000000000001 | 94 | 2 | 2.5000000000000001E-2 |  |  |  | 39.299999999999997 | 14.43 | 68 | 14 min | Alum | 0 |  | 2 | GAC | Anthracite | TOC @ CWRS
2023-01-25 10:12:00 AM | 176 | F2 |  | 6.02 | 0.128 | 0.22500000000000001 | 92.9 | 2 | 2.5000000000000001E-2 |  |  |  | 38.9 | 10.41 | 68 | 14 min | Alum | 0 |  | 2 | GAC | Anthracite | TOC @ CWRS
2023-01-26 09:41:00 AM | 177 | Raw |  | 5.69 | 0.41199999999999998 | 0.51100000000000001 | 73.5 | 26 |  | 0.04 |  |  |  |  | 60 | 14 min | Alum | 0 |  | 2 | GAC | Anthracite
2023-01-26 09:42:00 AM | 177 | DAF | 6.18 | 6.3 | 0.752 | 0.49 | 87.5 | 11 |  | 0.01 |  |  |  |  | 60 | 14 min | Alum | 0 |  | 2 | GAC | Anthracite
2023-01-26 09:44:00 AM | 177 | F1 |  | 6.22 | 5.0999999999999997E-2 | 0.109 | 95.2 | 1 |  | 0.01 |  |  | 1.6 | 14.21 | 60 | 14 min | Alum | 0 |  | 2 | GAC | Anthracite
2023-01-26 09:44:59 AM | 177 | F2 |  | 6.15 | 4.5999999999999999E-2 | 0.114 | 94 | 1 |  | 0.01 |  |  | 0.8 | 3.71 | 60 | 14 min | Alum | 0 |  | 2 | GAC | Anthracite
2023-01-26 11:13:00 AM | 178 | Raw |  | 5.7 | 0.42699999999999999 | 0.53200000000000003 | 73.400000000000006 | 25 | [6 empty] | 60 | 14 min | Alum | 0 |  | 2 | GAC | Anthracite | TOC @ CWRS
2023-01-26 11:14:00 AM | 178 | DAF | 6.28 | 6.28 | 0.42899999999999999 | 0.51200000000000001 | 87.4 | 10 | [6 empty] | 60 | 14 min | Alum | 0 |  | 2 | GAC | Anthracite | TOC @ CWRS
2023-01-26 11:14:59 AM | 178 | F1 |  | 6.22 | 3.7999999999999999E-2 | 0.105 | 95.6 | 1 |  |  |  |  | 2.9 | 14.33 | 60 | 14 min | Alum | 0 |  | 2 | GAC | Anthracite | TOC @ CWRS
2023-01-26 11:16:00 AM | 178 | F2 |  | 6.16 | 0.03 | 0.13100000000000001 | 94.5 | 1 |  |  |  |  | 2.1 | 3.89 | 60 | 14 min | Alum | 0 |  | 2 | GAC | Anthracite | TOC @ CWRS
2023-01-27 09:05:59 AM | 179 | Raw |  | 5.63 | 0.48399999999999999 | 0.57699999999999996 | 72 | 28 |  | 0.06 |  |  |  |  | 52 | 14 min | Alum | 0 |  | 2 | GAC | Anthracite | TOC @ CWRS
2023-01-27 09:06:59 AM | 179 | DAF | 6.42 | 6.46 | 0.52100000000000002 | 0.51400000000000001 | 86.7 | 14 |  | 0.02 |  |  |  |  | 52 | 14 min | Alum | 0 |  | 2 | GAC | Anthracite | TOC @ CWRS
2023-01-27 09:07:59 AM | 179 | F1 |  | 6.25 | 4.3999999999999997E-2 | 0.13300000000000001 | 96 | 2 |  | 0.01 |  |  | 5.2 | 14.48 | 52 | 14 min | Alum | 0 |  | 2 | GAC | Anthracite | TOC @ CWRS
2023-01-27 09:10:00 AM | 179 | F2 |  | 6.07 | 3.5000000000000003E-2 | 0.106 | 94.6 | 3 |  | 0.01 |  |  | 4.4000000000000004 | 3.89 | 52 | 14 min | Alum | 0 |  | 2 | GAC | Anthracite | TOC @ CWRS
2023-01-31 07:18:00 AM | 180 | Raw |  | 5.66 | 0.42599999999999999 | 0.50800000000000001 | 72.2 | 27 |  | 0.05 |  |  |  |  | 52 | 14 min | Alum | 0 |  | 2 | GAC | Anthracite
2023-01-31 07:19:00 AM | 180 | DAF | 6.36 | 6.53 | 0.39600000000000002 | 0.59899999999999998 | 85 | 15 |  | 0.02 |  |  |  |  | 52 | 14 min | Alum | 0 |  | 2 | GAC | Anthracite
2023-01-31 07:21:00 AM | 180 | F1 |  | 6.28 | 4.2000000000000003E-2 | 0.104 | 95 | 1 |  | 0.01 |  |  | 9.4 | 13.93 | 52 | 14 min | Alum | 0 |  | 2 | GAC | Anthracite
2023-01-31 07:22:00 AM | 180 | F2 |  | 6.17 | 3.2000000000000001E-2 | 0.109 | 93.2 | 1 |  | 0.01 |  |  | 8.6 | 4.18 | 52 | 14 min | Alum | 0 |  | 2 | GAC | Anthracite
2023-02-01 06:50:00 AM | 181 | Raw |  | 5.61 | 0.44 | 0.505 | 72.2 | 27 |  | 0.04 |  |  |  |  | 52 | 14 min | Alum | 0 |  | 2 | GAC | Anthracite
2023-02-01 06:50:59 AM | 181 | DAF | 6.57 | 6.41 | 0.42799999999999999 | 0.61199999999999999 | 84.2 | 16 |  | 0.02 |  |  |  |  | 52 | 14 min | Alum | 0 |  | 2 | GAC | Anthracite
2023-02-01 06:53:00 AM | 181 | F1 |  | 6.19 | 4.7E-2 | 0.10100000000000001 | 94.6 | 2 |  | 0.01 |  |  | 10.9 | 14.78 | 52 | 14 min | Alum | 0 |  | 2 | GAC | Anthracite
2023-02-01 06:55:00 AM | 181 | F2 |  | 6.02 | 3.1E-2 | 0.104 | 93.4 | 3 |  | 0.01 |  |  | 10.3 | 5.17 | 52 | 14 min | Alum | 0 |  | 2 | GAC | Anthracite
2023-02-01 08:00:00 AM | 182 | Raw |  | 5.62 | 0.44800000000000001 | 0.50900000000000001 | 72 | 27 | [6 empty] | 52 | 14 min | Alum | 0 |  | 2 | GAC | Anthracite
2023-02-01 08:03:00 AM | 182 | DAF | 6.67 | 6.32 | 0.39600000000000002 | 0.54 | 86.1 | 12 | [6 empty] | 52 | 14 min | Alum | 0 |  | 2 | GAC | Anthracite
2023-02-01 08:04:00 AM | 182 | F1 |  | 6.07 | 5.0999999999999997E-2 | 0.107 | 94.4 | 1 |  |  |  |  | 11.8 | 15 | 52 | 14 min | Alum | 0 |  | 2 | GAC | Anthracite
2023-02-01 08:05:00 AM | 182 | F2 |  | 6.03 | 3.1E-2 | 0.121 | 93.7 | 1 |  |  |  |  | 11.2 | 3.4 | 52 | 14 min | Alum | 0 |  | 2 | GAC | Anthracite
2023-02-01 09:56:00 AM | 183 | Raw |  | 5.58 | 0.45300000000000001 | 0.51400000000000001 | 72.099999999999994 | 27 | [6 empty] | 52 | 21 min | Alum | 0 |  | 2 | GAC | Anthracite | TOC @ CWRS
2023-02-01 09:56:59 AM | 183 | DAF | 6.68 | 6.09 | 0.34399999999999997 | 0.51800000000000002 | 87.1 | 11 | [6 empty] | 52 | 21 min | Alum | 0 |  | 2 | GAC | Anthracite | TOC @ CWRS
2023-02-01 09:58:59 AM | 183 | F1 |  | 6.07 | 4.1000000000000002E-2 | 0.10100000000000001 | 95.6 | 1 |  |  |  |  | 13.6 | 14.37 | 52 | 21 min | Alum | 0 |  | 2 | GAC | Anthracite | TOC @ CWRS
2023-02-01 10:00:00 AM | 183 | F2 |  | 5.98 | 0.03 | 0.113 | 94.1 | 1 |  |  |  |  | 13 | 5.39 | 52 | 21 min | Alum | 0 |  | 2 | GAC | Anthracite | TOC @ CWRS
2023-02-02 05:19:00 AM | 184 | Raw |  | 5.52 | 0.45200000000000001 | 0.50900000000000001 | 71.900000000000006 | 28 |  | 0.03 |  |  |  |  | 52 | 21 min | Alum | 0 |  | 2 | GAC | Anthracite
2023-02-02 05:20:00 AM | 184 | DAF | 6.7 | 6.15 | 0.34799999999999998 | 0.48499999999999999 | 86.9 | 11 |  | 0.02 |  |  |  |  | 52 | 21 min | Alum | 0 |  | 2 | GAC | Anthracite
2023-02-02 05:22:00 AM | 184 | F1 |  | 6.06 | 4.3999999999999997E-2 | 0.10100000000000001 | 95.2 | 2 |  | 0.01 |  |  | 31.1 | 15 | 52 | 21 min | Alum | 0 |  | 2 | GAC | Anthracite
2023-02-02 05:23:00 AM | 184 | F2 |  | 5.92 | 3.6999999999999998E-2 | 0.104 | 93.6 | 3 |  | 0.01 |  |  | 30.5 | 7.18 | 52 | 21 min | Alum | 0 |  | 2 | GAC | Anthracite
2023-02-02 08:38:00 AM | 185 | Raw |  | 5.57 | 0.442 | 0.51500000000000001 | 71.8 | 28 | [6 empty] | 44 | 21 min | Alum | 0 |  | 2 | GAC | Anthracite
2023-02-02 08:39:00 AM | 185 | DAF | 6.74 | 6.23 | 0.42299999999999999 | 0.77700000000000002 | 82.3 | 21 | [6 empty] | 44 | 21 min | Alum | 0 |  | 2 | GAC | Anthracite
2023-02-02 08:41:00 AM | 185 | F1 |  | 6.12 | 5.3999999999999999E-2 | 0.112 | 95.5 | 2 |  |  |  |  | 34 | 14.47 | 44 | 21 min | Alum | 0 |  | 2 | GAC | Anthracite
2023-02-02 08:42:00 AM | 185 | F2 |  | 6.09 | 5.6000000000000001E-2 | 0.13900000000000001 | 93.5 | 4 |  |  |  |  | 33.4 | 7.14 | 44 | 21 min | Alum | 0 |  | 2 | GAC | Anthracite
2023-02-02 10:41:00 AM | 186 | Raw |  | 5.62 | 0.44400000000000001 | 0.50700000000000001 | 71.8 | 27 | [6 empty] | 44 | 21 min | Alum | 0 |  | 2 | GAC | Anthracite | TOC @ CWRS
2023-02-02 10:41:59 AM | 186 | DAF | 6.76 | 6.33 | 0.44900000000000001 | 0.71499999999999997 | 83.1 | 18 | 2.8000000000000001E-2 | [5 empty] | 44 | 21 min | Alum | 0 |  | 2 | GAC | Anthracite | TOC @ CWRS
2023-02-02 10:43:00 AM | 186 | F1 |  | 6.08 | 7.4999999999999997E-2 | 0.14099999999999999 | 94 | 2 | 2.7E-2 |  |  |  | 35.9 | 15 | 44 | 21 min | Alum | 0 |  | 2 | GAC | Anthracite | TOC @ CWRS
2023-02-02 10:45:00 AM | 186 | F2 |  | 5.99 | 0.08 | 0.153 | 92.5 | 4 | 2.5999999999999999E-2 |  |  |  | 35.299999999999997 | 7.26 | 44 | 21 min | Alum | 0 |  | 2 | GAC | Anthracite | TOC @ CWRS
2023-03-08 05:39:00 AM | 187 | Raw |  | 5.46 | 0.39700000000000002 | 0.502 | 71.599999999999994 | 27 |  | 0.05 | 3.6999999999999998E-2 |  |  |  | 50 | 22 min | Alum | 0 |  | 2 | GAC | Anthracite
2023-03-08 05:41:00 AM | 187 | DAF | 6.51 | 6.03 | 0.32700000000000001 | 0.46100000000000002 | 88.5 | 11 |  | 0.02 | 0.41699999999999998 |  |  |  | 50 | 22 min | Alum | 0 |  | 2 | GAC | Anthracite
2023-03-08 07:37:00 AM | 188 | Raw |  | 5.49 | 0.40500000000000003 | 0.51700000000000002 | 71.7 | 28 | [6 empty] | 50 | 14 min | Alum | 0 |  | 2 | GAC | Anthracite
2023-03-08 07:38:00 AM | 188 | DAF | 6.65 | 6.22 | 0.42299999999999999 | 0.45200000000000001 | 88 | 12 |  | 0.02 | 0.315 |  |  |  | 50 | 14 min | Alum | 0 |  | 2 | GAC | Anthracite
2023-03-08 08:39:00 AM | 189 | Raw |  | 5.46 | 0.40400000000000003 | 0.53500000000000003 | 71.5 | 27 | [6 empty] | 50 | 14 min | Alum | 0 |  | 2 | GAC | Anthracite | TOC @ CWRS
2023-03-08 08:40:00 AM | 189 | DAF | 6.74 | 6.2 | 0.36 | 0.495 | 87.6 | 10 |  |  | 0.43099999999999999 |  |  |  | 50 | 14 min | Alum | 0 |  | 2 | GAC | Anthracite | TOC @ CWRS
2023-03-08 12:04:59 PM | 190 | Raw |  | 5.55 | 0.40500000000000003 | 0.498 | 71.2 | 27 | [6 empty] | 50 | 22 min | Alum | 0 |  | 2 | GAC | Anthracite | TOC @ CWRS
2023-03-08 12:06:00 PM | 190 | DAF | 6.62 | 6.39 | 0.34 | 0.57199999999999995 | 86.7 | 13 | [6 empty] | 50 | 22 min | Alum | 0 |  | 2 | GAC | Anthracite | TOC @ CWRS
2023-03-09 07:50:00 AM | 191 | Raw |  | 5.49 | 0.40600000000000003 | 0.48199999999999998 | 71.400000000000006 | 28 |  | 0.06 | 1.4999999999999999E-2 |  |  |  | 50 | 22 min | Alum | 0 |  | 2 | GAC | Anthracite | TOC @ CWRS
2023-03-09 07:49:00 AM | 191 | DAF | 6.67 | 6.09 | 0.32200000000000001 | 0.46100000000000002 | 88.8 | 9 |  | 0.01 |  |  |  |  | 50 | 22 min | Alum | 0 |  | 2 | GAC | Anthracite | TOC @ CWRS
2023-03-10 10:43:59 AM | 192 | Raw |  | 5.63 |  | 0.47599999999999998 | 71.400000000000006 | 28 |  | 0.06 | 4.2999999999999997E-2 |  |  |  | 50 | 22 min | Alum | 0 |  | 2 | GAC | Anthracite | TOC @ CWRS
2023-03-10 10:45:00 AM | 192 | DAF | 6.59 | 6.06 | 0.38 | 0.435 | 88.5 | 9 |  | 0.02 | 0.42099999999999999 |  |  |  | 50 | 22 min | Alum | 0 |  | 2 | GAC | Anthracite | TOC @ CWRS
2023-03-10 11:50:00 AM | 193 | Raw |  | 5.44 |  | 0.47799999999999998 | 71.400000000000006 | 27 | [6 empty] | 50 | 14 min | Alum | 0 |  | 2 | GAC | Anthracite
2023-03-10 11:51:00 AM | 193 | DAF | 6.65 | 5.96 | 0.48799999999999999 | 0.58399999999999996 | 86.7 | 12 |  |  | 0.42599999999999999 |  |  |  | 50 | 14 min | Alum | 0 |  | 2 | GAC | Anthracite | TOC @ CWRS
2023-03-13 09:17:00 AM | 194 | Raw |  | 5.4 |  | 0.47099999999999997 | 71.400000000000006 | 28 |  | 0.04 | 1.2E-2 |  |  |  | 50 | 14 min | Alum | 0 |  | 2 | GAC | Anthracite | TOC @ CWRS
2023-03-13 09:18:00 AM | 194 | DAF | 6.7 | 6.1 | 0.442 | 0.57999999999999996 | 87.1 | 14 |  | 0.02 | 0.39900000000000002 |  |  |  | 50 | 14 min | Alum | 0 |  | 2 | GAC | Anthracite | TOC @ CWRS
2023-03-13 12:17:00 PM | 195 | Raw |  | 5.56 |  | 0.46600000000000003 | 71.400000000000006 | 24 | [6 empty] | 50 | 14 min | Alum | 0 |  | 2 | GAC | Anthracite
2023-03-13 12:18:00 PM | 195 | DAF | 6.74 | 6.36 | 0.622 | 0.52 | 86.1 | 9 | [6 empty] | 50 | 14 min | Alum | 0 |  | 2 | GAC | Anthracite
2023-03-14 06:47:00 AM | 196 | Raw |  | 5.48 |  | 0.45900000000000002 | 71.400000000000006 | 28 |  | 0.06 | 8.0000000000000002E-3 |  |  |  | 50 | 7 min | Alum | 0 |  | 2 | GAC | Anthracite
2023-03-14 06:48:00 AM | 196 | DAF | 6.72 | 6.27 | 0.60899999999999999 | 0.65300000000000002 | 84.1 | 16 |  | 0.03 | 0.38100000000000001 |  |  |  | 50 | 7 min | Alum | 0 |  | 2 | GAC | Anthracite
2023-03-14 07:44:59 AM | 197 | Raw |  | 5.48 |  | 0.46500000000000002 | 71.400000000000006 | 27 | [6 empty] | 50 | 7 min | Alum | 0 |  | 2 | GAC | Anthracite | TOC @ CWRS
2023-03-14 07:46:00 AM | 197 | DAF | 6.8 | 6.26 | 0.69699999999999995 | 0.58899999999999997 | 85.7 | 13 |  |  | 0.38300000000000001 |  |  |  | 50 | 7 min | Alum | 0 |  | 2 | GAC | Anthracite | TOC @ CWRS
2023-03-14 11:01:00 AM | 198 | Raw |  | 5.44 |  | 0.47899999999999998 | 71.400000000000006 | 27 | [6 empty] | 59 | 7 min | Alum | 0 |  | 2 | GAC | Anthracite
2023-03-14 11:03:00 AM | 198 | DAF | 6.93 | 6.61 | 0.51500000000000001 | 0.61399999999999999 | 83.5 | 15 |  |  | 0.40400000000000003 |  |  |  | 59 | 7 min | Alum | 0 |  | 2 | GAC | Anthracite
2023-03-14 11:47:00 AM | 199 | Raw |  | 5.45 |  | 0.46400000000000002 | 71.400000000000006 | 28 | [6 empty] | 59 | 7 min | Alum | 0 |  | 2 | GAC | Anthracite | TOC @ CWRS
2023-03-14 11:48:00 AM | 199 | DAF | 6.94 | 6.34 | 0.49099999999999999 | 0.56899999999999995 | 85.8 | 14 |  |  | 0.40799999999999997 |  |  |  | 59 | 7 min | Alum | 0 |  | 2 | GAC | Anthracite | TOC @ CWRS
2023-03-14 12:19:59 PM | 200 | Raw |  | 5.45 |  | 0.47399999999999998 | 71.400000000000006 | 27 | [6 empty] | 59 | 7 min | Alum | 0 |  | 2 | GAC | Anthracite
2023-03-14 12:21:00 PM | 200 | DAF | 6.95 | 6.32 | 0.53800000000000003 | 0.56799999999999995 | 85.7 | 13 | [6 empty] | 59 | 7 min | Alum | 0 |  | 2 | GAC | Anthracite
2023-03-15 06:48:00 AM | 201 | Raw |  | 5.47 |  | 0.46300000000000002 | 71.5 | 28 |  | 0.05 | 3.1E-2 |  |  |  | 68 | 7 min | Alum | 0 |  | 2 | GAC | Anthracite
2023-03-15 06:49:00 AM | 201 | DAF | 6.72 | 6.45 | 0.44900000000000001 | 0.61 | 85.5 | 14 |  | 0.02 | 0.41699999999999998 |  |  |  | 68 | 7 min | Alum | 0 |  | 2 | GAC | Anthracite
2023-03-15 08:25:00 AM | 202 | Raw |  | 5.35 |  | 0.46400000000000002 | 71.400000000000006 | 28 | [6 empty] | 68 | 7 min | Alum | 0 |  | 2 | GAC | Anthracite | TOC @ CWRS
2023-03-15 08:26:00 AM | 202 | DAF | 6.86 | 6.35 | 0.38 | 0.56799999999999995 | 85.2 | 14 |  |  | 0.39800000000000002 |  |  |  | 68 | 7 min | Alum | 0 |  | 2 | GAC | Anthracite | TOC @ CWRS
2023-03-15 10:12:00 AM | 203 | Raw |  | 5.44 |  | 0.46899999999999997 | 71.5 | 27 | [6 empty] | 77 | 7 min | Alum | 0 |  | 2 | GAC | Anthracite
2023-03-15 10:13:00 AM | 203 | DAF | 6.92 | 6.49 | 0.35299999999999998 | 0.59499999999999997 | 85.2 | 14 |  |  | 0.40899999999999997 |  |  |  | 77 | 7 min | Alum | 0 |  | 2 | GAC | Anthracite
2023-03-15 11:39:00 AM | 204 | Raw |  | 5.42 |  | 0.48499999999999999 | 71.5 | 27 | [6 empty] | 77 | 7 min | Alum | 0 |  | 2 | GAC | Anthracite
2023-03-15 11:40:00 AM | 204 | DAF | 6.95 | 6.46 | 0.34599999999999997 | 0.52800000000000002 | 86.3 | 11 |  |  | 0.41099999999999998 |  |  |  | 77 | 7 min | Alum | 0 |  | 2 | GAC | Anthracite | TOC @ CWRS
2023-03-16 07:58:00 AM | 205 | Raw |  | 5.53 |  | 0.47199999999999998 | 71.2 | 28 |  | 0.04 | 5.6000000000000001E-2 |  |  |  | 86 | 7 min | Alum | 0 |  | 2 | GAC | Anthracite
2023-03-16 08:00:00 AM | 205 | DAF |  | 6.48 | 0.36199999999999999 | 0.54700000000000004 | 86 | 14 |  | 0.03 | 0.40200000000000002 |  |  |  | 86 | 7 min | Alum | 0 |  | 2 | GAC | Anthracite
2023-03-16 08:56:00 AM | 206 | Raw |  | 5.47 |  | 0.47699999999999998 | 71.3 | 28 | [6 empty] | 86 | 7 min | Alum | 0 |  | 2 | GAC | Anthracite | TOC @ CWRS
2023-03-16 08:57:00 AM | 206 | DAF | 6.67 | 6.37 | 0.33700000000000002 | 0.51500000000000001 | 86.4 | 12 |  |  | 0.42899999999999999 |  |  |  | 86 | 7 min | Alum | 0 |  | 2 | GAC | Anthracite | TOC @ CWRS
2023-03-16 10:28:00 AM | 207 | Raw |  | 5.43 |  | 0.47499999999999998 | 71.3 | 28 | [6 empty] | 95 | 7 min | Alum | 0 |  | 2 | GAC | Anthracite
2023-03-16 10:29:00 AM | 207 | DAF | 6.83 | 6.35 | 0.33400000000000002 | 0.45600000000000002 | 87.4 | 12 |  |  | 0.39100000000000001 |  |  |  | 95 | 7 min | Alum | 0 |  | 2 | GAC | Anthracite
2023-03-16 11:20:59 AM | 208 | Raw |  | 5.45 |  | 0.46800000000000003 | 71.400000000000006 | 28 | [6 empty] | 95 | 7 min | Alum | 0 |  | 2 | GAC | Anthracite
2023-03-16 11:21:59 AM | 208 | DAF | 6.88 | 6.39 | 0.35199999999999998 | 0.46300000000000002 | 87.5 | 11 |  |  | 0.40400000000000003 |  |  |  | 95 | 7 min | Alum | 0 |  | 2 | GAC | Anthracite | TOC @ CWRS
2023-03-20 07:38:00 AM | 209 | Raw |  | 5.42 |  | 0.46800000000000003 | 71.5 | 25 |  | 0.06 | 4.2000000000000003E-2 |  |  |  | 104 | 7 min | Alum | 0 |  | 2 | GAC | Anthracite
2023-03-20 07:39:00 AM | 209 | DAF | 6.72 | 6.3 | 0.36399999999999999 | 0.46500000000000002 | 87.8 | 9 |  | 0.02 | * |  |  |  | 104 | 7 min | Alum | 0 |  | 2 | GAC | Anthracite
2023-03-20 08:43:00 AM | 210 | Raw |  | 5.41 |  | 0.45600000000000002 | 71.400000000000006 | 27 | [6 empty] | 104 | 7 min | Alum | 0 |  | 2 | GAC | Anthracite | TOC @ CWRS
2023-03-20 08:44:00 AM | 210 | DAF | 6.77 | 6.16 | 0.373 | 0.495 | 87.8 | 10 |  |  | 0.41199999999999998 |  |  |  | 104 | 7 min | Alum | 0 |  | 2 | GAC | Anthracite | TOC @ CWRS
2023-03-20 12:01:00 PM | 211 | Raw |  | 5.44 |  | 0.47 | 71.3 | 27 | [6 empty] | 104 | 14 min | Alum | 0 |  | 2 | GAC | Anthracite
2023-03-20 12:02:00 PM | 211 | DAF | 6.67 | 6.29 | 0.30399999999999999 | 0.41599999999999998 | 88.8 | 10 |  |  | 0.42699999999999999 |  |  |  | 104 | 14 min | Alum | 0 |  | 2 | GAC | Anthracite | TOC @ CWRS
2023-03-21 07:16:00 AM | 212 | Raw |  | 5.43 |  | 0.45800000000000002 | 71.5 | 28 |  | 7.0000000000000007E-2 | 3.4000000000000002E-2 |  |  |  | 104 | 22 min | Alum | 0 |  | 2 | GAC | Anthracite
2023-03-21 07:17:00 AM | 212 | DAF | 6.61 | 6.24 | 0.27800000000000002 | 0.432 | 88.7 | 11 |  | 0.02 | 0.38500000000000001 |  |  |  | 104 | 22 min | Alum | 0 |  | 2 | GAC | Anthracite
2023-03-21 08:13:00 AM | 213 | Raw |  | 5.43 |  | 0.46600000000000003 | 71.400000000000006 | 28 | [6 empty] | 104 | 22 min | Alum | 0 |  | 2 | GAC | Anthracite | TOC @ CWRS
2023-03-21 08:14:00 AM | 213 | DAF | 6.67 | 6.22 | 0.26900000000000002 | 0.38400000000000001 | 89.4 | 8 |  |  | 0.40400000000000003 |  |  |  | 104 | 22 min | Alum | 0 |  | 2 | GAC | Anthracite | TOC @ CWRS
2023-03-21 09:56:00 AM | 214 | Raw |  | 5.45 |  | 0.45400000000000001 | 71.400000000000006 | 28 | [6 empty] | 95 | 22 min | Alum | 0 |  | 2 | GAC | Anthracite
2023-03-21 09:56:59 AM | 214 | DAF | 6.72 | 6.22 | 0.251 | 0.34699999999999998 | 89.6 | 7 |  |  | 0.36499999999999999 |  |  |  | 95 | 22 min | Alum | 0 |  | 2 | GAC | Anthracite
2023-03-21 10:48:00 AM | 215 | Raw |  | 5.47 |  | 0.44900000000000001 | 71.400000000000006 | 27 | [6 empty] | 95 | 22 min | Alum | 0 |  | 2 | GAC | Anthracite
2023-03-21 10:49:00 AM | 215 | DAF | 6.73 | 6.24 | 0.246 | 0.38300000000000001 | 89.5 | 9 |  |  | 0.435 |  |  |  | 95 | 22 min | Alum | 0 |  | 2 | GAC | Anthracite | TOC @ CWRS
2023-03-22 08:59:00 AM | 216 | Raw |  | 5.57 |  | 0.46200000000000002 | 71.400000000000006 | 29 |  | 0.05 | 3.4000000000000002E-2 |  |  |  | 86 | 22 min | Alum | 0 |  | 2 | GAC | Anthracite
2023-03-22 08:59:59 AM | 216 | DAF | 6.73 | 6.28 | 0.29099999999999998 | 0.42 | 88.5 | 10 |  | 0.02 | 0.42199999999999999 |  |  |  | 86 | 22 min | Alum | 0 |  | 2 | GAC | Anthracite
2023-03-22 09:48:00 AM | 217 | Raw |  | 5.46 |  | 0.45500000000000002 | 71.599999999999994 | 27 | [6 empty] | 86 | 22 min | Alum | 0 |  | 2 | GAC | Anthracite | TOC @ CWRS
2023-03-22 09:48:59 AM | 217 | DAF | 6.75 | 6.19 | 0.27 | 0.39900000000000002 | 88.7 | 9 |  |  | 0.41499999999999998 |  |  |  | 86 | 22 min | Alum | 0 |  | 2 | GAC | Anthracite | TOC @ CWRS
2023-03-22 11:35:00 AM | 218 | Raw |  | 5.46 |  | 0.44800000000000001 | 71.599999999999994 | 28 | [6 empty] | 77 | 22 min | Alum | 0 |  | 2 | GAC | Anthracite
2023-03-22 11:36:00 AM | 218 | DAF | 6.79 | 6.28 | 0.249 | 0.374 | 89.2 | 10 |  |  | 0.38900000000000001 |  |  |  | 77 | 22 min | Alum | 0 |  | 2 | GAC | Anthracite
2023-03-22 12:08:59 PM | 219 | Raw |  | 5.48 |  | 0.45 | 71.5 | 28 | [6 empty] | 77 | 22 min | Alum | 0 |  | 2 | GAC | Anthracite
2023-03-22 12:10:00 PM | 219 | DAF | 6.79 | 6.32 | 0.25600000000000001 | 0.38100000000000001 | 89.1 | 8 |  |  | 0.39 |  |  |  | 77 | 22 min | Alum | 0 |  | 2 | GAC | Anthracite | TOC @ CWRS
2023-03-23 07:27:00 AM | 220 | Raw |  | 5.45 |  | 0.44600000000000001 | 71.7 | 29 |  | 7.0000000000000007E-2 | 2.5999999999999999E-2 |  |  |  | 68 | 22 min | Alum | 0 |  | 2 | GAC | Anthracite
2023-03-23 07:28:00 AM | 220 | DAF | 6.83 | 6.29 | 0.27400000000000002 | 0.38900000000000001 | 88.9 | 11 |  | 0.02 | 0.41 |  |  |  | 68 | 22 min | Alum | 0 |  | 2 | GAC | Anthracite
2023-03-23 08:45:00 AM | 221 | Raw |  | 5.39 |  | 0.54500000000000004 | 71.400000000000006 | 29 | [6 empty] | 68 | 22 min | Alum | 0 |  | 2 | GAC | Anthracite | TOC @ CWRS
2023-03-23 08:46:00 AM | 221 | DAF | 6.83 | 6.22 | 0.26600000000000001 | 0.39900000000000002 | 89.2 | 10 |  |  | 0.39200000000000002 |  |  |  | 68 | 22 min | Alum | 0 |  | 2 | GAC | Anthracite | TOC @ CWRS
2023-03-23 11:01:00 AM | 222 | Raw |  | 5.44 |  | 0.47 | 71.400000000000006 | 28 | [6 empty] | 59 | 22 min | Alum | 0 |  | 2 | GAC | Anthracite
2023-03-23 11:02:00 AM | 222 | DAF | 6.88 | 6.25 | 0.29099999999999998 | 0.504 | 87.4 | 11 |  |  | 0.40699999999999997 |  |  |  | 59 | 22 min | Alum | 0 |  | 2 | GAC | Anthracite
2023-03-23 11:55:00 AM | 223 | Raw |  | 5.44 |  | 0.46600000000000003 | 71.5 | 26 | [6 empty] | 59 | 22 min | Alum | 0 |  | 2 | GAC | Anthracite
2023-03-23 11:56:00 AM | 223 | DAF | 6.86 | 6.19 | 0.28199999999999997 | 0.45200000000000001 | 87.6 | 9 |  |  | * |  |  |  | 59 | 22 min | Alum | 0 |  | 2 | GAC | Anthracite | TOC @ CWRS
2023-03-24 07:21:00 AM | 224 | Raw |  | 5.3 |  | 0.45200000000000001 | 71.5 | 28 |  | 0.05 | 2.5999999999999999E-2 |  |  |  | 50 | 22 min | Alum | 0 |  | 2 | GAC | Anthracite
2023-03-24 07:22:00 AM | 224 | DAF | 6.89 | 6.23 | 0.39900000000000002 | 0.69599999999999995 | 83.6 | 19 |  | 0.02 | 0.40500000000000003 |  |  |  | 50 | 22 min | Alum | 0 |  | 2 | GAC | Anthracite
2023-03-24 08:28:59 AM | 225 | Raw |  | 5.29 |  | 0.45600000000000002 | 71.599999999999994 | 27 | [6 empty] | 50 | 22 min | Alum | 0 |  | 2 | GAC | Anthracite | TOC @ CWRS
2023-03-24 08:30:00 AM | 225 | DAF | 6.93 | 6.25 | 0.378 | 0.61 | 85.1 | 15 |  |  | 0.38700000000000001 |  |  |  | 50 | 22 min | Alum | 0 |  | 2 | GAC | Anthracite | TOC @ CWRS
2023-03-24 10:10:00 AM | 226 | Raw |  | 5.32 |  | 0.44800000000000001 | 71.5 | 28 | [6 empty] | 45 | 22 min | Alum | 0 |  | 2 | GAC | Anthracite
2023-03-24 10:11:00 AM | 226 | DAF | 6.91 | 6.12 | 0.40200000000000002 | 0.75700000000000001 | 83.3 | 19 |  |  | 0.40500000000000003 |  |  |  | 45 | 22 min | Alum | 0 |  | 2 | GAC | Anthracite
2023-03-24 11:10:00 AM | 227 | Raw |  | 5.31 |  | 0.46600000000000003 | 71.5 | 27 | [6 empty] | 45 | 22 min | Alum | 0 |  | 2 | GAC | Anthracite
2023-03-24 11:11:00 AM | 227 | DAF | 6.91 | 6.3 | 0.38 | 0.73699999999999999 | 83.6 | 17 |  |  | 0.40300000000000002 |  |  |  | 45 | 22 min | Alum | 0 |  | 2 | GAC | Anthracite | TOC @ CWRS
2023-03-27 07:42:59 AM | 228 | Raw |  | 5.57 |  | 0.48199999999999998 | 71.5 | 27 |  | 0.06 | 3.4000000000000002E-2 |  |  |  | 41 | 22 min | Alum | 0 |  | 2 | GAC | Anthracite
2023-03-27 07:44:00 AM | 228 | DAF | 6.63 | 6.28 | 0.623 | 1.02 | 78.599999999999994 | 25 |  | 0.04 | 0.41699999999999998 |  |  |  | 41 | 22 min | Alum | 0 |  | 2 | GAC | Anthracite
2023-03-27 08:39:00 AM | 229 | Raw |  | 5.38 |  | 0.46700000000000003 | 71.599999999999994 | 28 | [6 empty] | 41 | 22 min | Alum | 0 |  | 2 | GAC | Anthracite | TOC @ CWRS
2023-03-27 08:40:00 AM | 229 | DAF | 6.68 | 6.35 | 0.55300000000000005 | 0.98 | 78.8 | 26 |  |  | 0.38800000000000001 |  |  |  | 41 | 22 min | Alum | 0 |  | 2 | GAC | Anthracite | TOC @ CWRS
2023-03-27 10:48:00 AM | 230 | Raw |  | 5.52 |  | 0.45500000000000002 | 71.5 | 27 | [6 empty] | 41 | 14 min | Alum | 0 |  | 2 | GAC | Anthracite
2023-03-27 10:49:00 AM | 230 | DAF | 6.76 | 6.61 | 0.56599999999999995 | 0.88800000000000001 | 80.3 | 23 |  |  | 0.39200000000000002 |  |  |  | 41 | 14 min | Alum | 0 |  | 2 | GAC | Anthracite
2023-03-27 11:48:00 AM | 231 | Raw |  | 5.48 |  | 0.45200000000000001 | 71.400000000000006 | 28 | [6 empty] | 41 | 14 min | Alum | 0 |  | 2 | GAC | Anthracite
2023-03-27 11:49:00 AM | 231 | DAF | 6.81 | 6.44 | 0.48099999999999998 | 0.72199999999999998 | 82.4 | 19 |  |  | 0.39600000000000002 |  |  |  | 41 | 14 min | Alum | 0 |  | 2 | GAC | Anthracite | TOC @ CWRS
2023-03-28 08:37:00 AM | 232 | Raw |  | 5.51 |  | 0.46 | 71.400000000000006 | 30 |  | 0.04 | 0.03 |  |  |  | 41 | 22 min | Alum | 0 |  | 2 | GAC | Anthracite
2023-03-28 08:38:00 AM | 232 | DAF | 6.97 | 6.57 | 0.47799999999999998 | 0.88900000000000001 | 79.900000000000006 | 26 |  | 0.03 | 0.39500000000000002 |  |  |  | 41 | 22 min | Alum | 0 |  | 2 | GAC | Anthracite
2023-03-28 09:23:00 AM | 233 | Raw |  | 5.48 |  | 0.45500000000000002 | 71.7 | 27 | [6 empty] | 41 | 22 min | Alum | 0 |  | 2 | GAC | Anthracite
2023-03-28 09:24:00 AM | 233 | DAF | 6.97 | 6.51 | 0.42399999999999999 | 0.874 | 81.099999999999994 | 21 |  |  | 0.38500000000000001 |  |  |  | 41 | 22 min | Alum | 0 |  | 2 | GAC | Anthracite
2023-03-28 11:06:00 AM | 234 | Raw |  | 5.44 |  | 0.46700000000000003 | 71.5 | 28 | [6 empty] | 41 | 14 min | Alum | 0 |  | 2 | GAC | Anthracite
2023-03-28 11:07:00 AM | 234 | DAF | 6.98 | 6.35 | 0.434 | 0.71499999999999997 | 83 | 18 |  |  | 0.41799999999999998 |  |  |  | 41 | 14 min | Alum | 0 |  | 2 | GAC | Anthracite
2023-03-29 05:20:00 AM | 235 | Raw |  | 5.39 |  | 0.45700000000000002 | 71.599999999999994 | 28 |  | 0.05 | 6.0999999999999999E-2 |  |  |  | 41 | 7 min | Alum | 0 |  | 2 | GAC | Anthracite
2023-03-29 05:20:59 AM | 235 | DAF | 6.98 | 6.27 | 0.54700000000000004 | 0.80800000000000005 | 80.900000000000006 | 21 |  | 0.03 | 0.375 |  |  |  | 41 | 7 min | Alum | 0 |  | 2 | GAC | Anthracite
2023-03-29 06:45:00 AM | 236 | Raw |  | 5.38 |  | 0.45600000000000002 | 71.7 | 28 | [6 empty] | 41 | 7 min | Alum | 0 |  | 2 | GAC | Anthracite | TOC @ CWRS
2023-03-29 06:46:00 AM | 236 | DAF | 6.96 | 6.37 | 0.55600000000000005 | 0.80100000000000005 | 81.400000000000006 | 21 |  |  | 0.38700000000000001 |  |  |  | 41 | 7 min | Alum | 0 |  | 2 | GAC | Anthracite | TOC @ CWRS
2023-03-29 08:31:00 AM | 237 | Raw |  | 5.43 |  | 0.45500000000000002 | 71.7 | 27 | [6 empty] | 50 | 7 min | Alum | 0 |  | 2 | GAC | Anthracite
2023-03-29 08:32:00 AM | 237 | DAF | 6.95 | 6.27 | 0.45 | 0.61699999999999999 | 84.2 | 15 |  |  | 0.41099999999999998 |  |  |  | 50 | 7 min | Alum | 0 |  | 2 | GAC | Anthracite
2023-03-29 09:32:00 AM | 238 | Raw |  | 5.39 |  | 0.45500000000000002 | 71.7 | 27 | [6 empty] | 50 | 7 min | Alum | 0 |  | 2 | GAC | Anthracite
2023-03-29 09:33:00 AM | 238 | DAF | 6.95 | 6.19 | 0.45200000000000001 | 0.66900000000000004 | 83.9 | 14 |  |  | 0.39200000000000002 |  |  |  | 50 | 7 min | Alum | 0 |  | 2 | GAC | Anthracite | TOC @ CWRS
2023-03-30 05:18:00 AM | 239 | Raw |  | 5.4 |  | 0.46600000000000003 | 71.599999999999994 | 27 |  | 0.05 | 3.9E-2 |  |  |  | 50 | 14 min | Alum | 0 |  | 2 | GAC | Anthracite
2023-03-30 05:19:00 AM | 239 | DAF | 6.91 | 6.34 | 0.35399999999999998 | 0.51600000000000001 | 86.3 | 13 |  | 0.03 | 0.38200000000000001 |  |  |  | 50 | 14 min | Alum | 0 |  | 2 | GAC | Anthracite
2023-03-30 06:33:00 AM | 240 | Raw |  | 5.41 |  | 0.47799999999999998 | 71.7 | 29 | [6 empty] | 50 | 14 min | Alum | 0 |  | 2 | GAC | Anthracite | TOC @ CWRS
2023-03-30 06:38:00 AM | 240 | DAF | 6.89 | 6.25 | 0.36799999999999999 | 0.59299999999999997 | 86 | 15 |  |  | 0.374 |  |  |  | 50 | 14 min | Alum | 0 |  | 2 | GAC | Anthracite | TOC @ CWRS
2023-03-30 09:03:00 AM | 241 | Raw |  | 5.41 |  | 0.47199999999999998 | 71.7 | 27 | [6 empty] | 50 | 22 min | Alum | 0 |  | 2 | GAC | Anthracite
2023-03-30 09:03:59 AM | 241 | DAF | 6.88 | 6.35 | 0.37 | 0.60899999999999999 | 85.2 | 15 |  |  | 0.40300000000000002 |  |  |  | 50 | 22 min | Alum | 0 |  | 2 | GAC | Anthracite
2023-03-30 09:48:00 AM | 242 | Raw |  | 5.41 |  | 0.45700000000000002 | 71.900000000000006 | 27 | [6 empty] | 50 | 22 min | Alum | 0 |  | 2 | GAC | Anthracite
2023-03-30 09:48:59 AM | 242 | DAF | 6.88 | 6.37 | 0.36599999999999999 | 0.63500000000000001 | 85.3 | 14 |  |  | 0.39800000000000002 |  |  |  | 50 | 22 min | Alum | 0 |  | 2 | GAC | Anthracite | TOC @ CWRS